## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Top Energy Limited
| Disclosure Date | 2026-08-30
| Disclosure Year (year ended) | 2026-03-31
Template for Schedule 10a
Prepared 19 February 2026.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Targeted Review 2024) Amendment Determination 2024 [2024] NZCC 2.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Top Energy
[15 empty] | For Year Ended | 2026-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | INCD-1121-J-OXFORD STREET | Okahu CB1108 - Oxford Street |  | OXFORD STREET | 2025-07-30 10:00 | 45868.4167 | 2025-07-30 14:51 | 45868.6188 | 1.2385 | 0.0047086 | 170 | 44713.6333 | Planned | Planned Outage | # Commissioned Ring Mains RM247, RM281, South Rd, Kaitaia
10 |  | INCD-1127-J-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-09-01 00:04 | 45901.0028 | 2025-09-01 06:42 | 45901.2792 | 3.252 | 0.0081708 | 295 | 117410 | Unplanned | Unknown | # Sectionaliser Tripped S1099, Foreshore Rd, Kaikohe
11 |  | INCD-1130-J-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-10-20 14:46 | 45950.6153 | 2025-10-20 15:19 | 45950.6382 | 0.0018281 | 5.5396e-05 | 2 | 66 | Planned | Planned Outage | # Commissioning New Voltage Regulator 19, Maromaku Rd, Kawakawa
12 |  | INCD-1136-J-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2026-02-13 13:05 | 46066.5451 | 2026-02-13 17:07 | 46066.7132 | 0.046588 | 0.00027698 | 10 | 1682 | Unplanned | Lightning | # Multiple Transformer Fuses Blown due to Lightning near F2181, Orakau Rd, Kaikohe
13 |  | INCD-1142-J-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2026-03-17 09:31 | 46098.3965 | 2026-03-17 16:48 | 46098.7 | 0.28052 | 0.00069244 | 25 | 10128 | Planned | Planned Outage | # Upgrade Conductor, Pole 405037, Manawaora Rd, Kawakawa
14 |  | INCD-1148-J-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2026-03-18 10:02 | 46099.4181 | 2026-03-18 13:00 | 46099.5417 | 0.019721 | 0.00011079 | 4 | 712 | Planned | Planned Outage | # Replace Poles, Crossarms, Beyond L208, Ruapekapeka Rd, Kawakawa
15 |  | INCD-29846-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-04-01 09:43 | 45748.4049 | 2025-04-01 11:49 | 45748.4924 | 0.045369 | 0.00036007 | 13 | 1638 | Planned | Planned Outage | # Install Fuses, F2426, at Pole 430339, Manukau Rd, Herekino
16 |  | INCD-30017-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-04-01 13:08 | 45748.5472 | 2025-04-01 15:12 | 45748.6333 | 0.048083 | 0.00038777 | 14 | 1736 | Planned | Planned Outage | # New Fuses F2422, Pole 430439, Rangikohu Rd, Herekino
17 |  | INCD-30131-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-04-29 10:10 | 45776.4236 | 2025-04-29 14:16 | 45776.5944 | 0.27027 | 0.0011356 | 41 | 9758 | Planned | Planned Outage | # Replace Span of Line, from Pole 423887, SH1, Towai
18 |  | INCD-30143-F-TAU BLOCK | Moerewa 031372 - Tau Block |  | TAU BLOCK | 2025-04-10 09:09 | 45757.3812 | 2025-04-10 14:22 | 45757.5986 | 0.026008 | 8.3093e-05 | 3 | 939 | Planned | Planned Outage | # Replace Multiple Poles 424992 to 424978, McIntyre Rd, Moerewa
19 |  | INCD-30164-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-04-08 09:36 | 45755.4 | 2025-04-08 14:47 | 45755.616 | 0.3116 | 0.0011079 | 40 | 11250 | Planned | Planned Outage | # Replace Burnt Crossarm, at Pole 435893, Otaipango Rd, Pukenui
20 |  | INCD-30173-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-04-10 10:26 | 45757.4347 | 2025-04-10 14:50 | 45757.6181 | 0.22269 | 0.00091403 | 33 | 8040 | Planned | Planned Outage | # Replace Transformer T02934, Motuti Rd, Panguru
21 |  | INCD-30215-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2025-04-14 09:25 | 45761.3924 | 2025-04-14 14:12 | 45761.5917 | 0.31002 | 0.0010802 | 39 | 11193 | Planned | Planned Outage | # New Connection, Replace Pole 403030, Scoresby Street, Opua
22 |  | INCD-30269-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-04-02 15:06 | 45749.6292 | 2025-04-02 16:16 | 45749.6778 | 0.21521 | 0.0030745 | 111 | 7770 | Unplanned | Defective Equipment | # Broken Lead at Link L1043, SH12, Pakanae
23 |  | INCD-30272-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-04-03 06:23 | 45750.266 | 2025-04-03 08:15 | 45750.3438 | 0.59532 | 0.0070629 | 255 | 21493.4333 | Unplanned | Vegetation | # Tree Contact Tripped Sectionaliser S1007, Kerikeri Inlet Rd, Kerikeri
24 |  | INCD-30281-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-04-03 08:24 | 45750.3502 | 2025-04-03 09:14 | 45750.3844 | 0.47126 | 0.0095557 | 345 | 17014.25 | Unplanned | Vegetation | # Tree Branch Fell on Line, at Pole 435643, Far North Rd, Ngataki
25 |  | INCD-30299-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-04-03 17:29 | 45750.7285 | 2025-04-03 20:05 | 45750.8368 | 0.086417 | 0.00055396 | 20 | 3120 | Unplanned | Vegetation | # Branch Contacted Line, at Pole 413258, Renwick Road, Omanaia
26 |  | INCD-30302-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-04-03 19:20 | 45750.8056 | 2025-04-03 23:31 | 45750.9799 | 0.29199 | 0.0011633 | 42 | 10542 | Unplanned | Defective Equipment | # Flipped Crossarm, at Pole 428696, Poko Pohaia Rd, Awanui
27 |  | INCD-30305-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-04-04 01:30 | 45751.0623 | 2025-04-04 09:17 | 45751.3868 | 3.1505 | 0.0093341 | 337 | 113746.1667 | Unplanned | Vegetation | # Tree through Lines, at Pole 416309, Mangakahia Rd, Kaikohe
28 |  | INCD-30308-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-04-04 01:50 | 45751.0764 | 2025-04-04 06:10 | 45751.2569 | 1.3467 | 0.0051795 | 187 | 48620 | Unplanned | Defective Equipment | # Failed Joint, Pole 416023, Mangakahia Rd, Kaikohe
29 |  | INCD-30311-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-04-04 04:23 | 45751.1825 | 2025-04-04 08:50 | 45751.3681 | 0.84239 | 0.0055119 | 199 | 30413.5667 | Unplanned | Vegetation | # Broken Crossarm, Pole 440721, Wakelin Rd, Puketona
30 |  | INCD-30317-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-04-04 04:42 | 45751.1958 | 2025-04-04 18:45 | 45751.7812 | 0.84002 | 0.0029083 | 70 | 30328 | Unplanned | Defective Equipment | # Broken Binder on SWER at Pole 406036, Taita Rd, Waimamaku
31 |  | INCD-30326-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-04-04 10:12 | 45751.4251 | 2025-04-04 11:15 | 45751.4688 | 0.40571 | 0.0064536 | 233 | 14647.9333 | Unplanned | Vegetation | # Tree on Line at Pole 423970, Taupo Bay Road, Taipa
32 |  | INCD-30329-F-MATAURI BAY | Kaeo 191732 - Matauri Bay |  | MATAURI BAY | 2025-04-04 11:55 | 45751.4965 | 2025-04-05 13:17 | 45752.5535 | 2.2585 | 0.020635 | 389 | 81539.55 | Unplanned | Defective Equipment | # Faulty Switch 1031, RMU 119, Matauri Bay
33 |  | INCD-30395-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-05-02 09:15 | 45779.3854 | 2025-05-02 12:42 | 45779.5292 | 0.24396 | 0.0013295 | 48 | 8808 | Planned | Planned Outage | # Upgrade Pole 431923, Te Ahu Ahu Rd, Waimate North, Kaikohe
34 |  | INCD-30407-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-04-30 09:39 | 45777.4021 | 2025-04-30 13:18 | 45777.5542 | 0.35182 | 0.0016065 | 58 | 12702 | Planned | Planned Outage | # Install Sectionaliser S1071, Links, at Pole 48348
35 |  | INCD-30416-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-04-07 14:47 | 45754.6158 | 2025-04-07 15:52 | 45754.6615 | 0.8986 | 0.020995 | 758 | 32442.9667 | Unplanned | Other Cause | # Fire in Vegetation under 11kV Lines, SH10, Mangonui
36 |  | INCD-30425-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-04-08 08:46 | 45755.3653 | 2025-04-08 11:13 | 45755.4674 | 0.1425 | 0.00096942 | 35 | 5145 | Unplanned | Wildlife | # Bird Strike, Pole 419311, Dutton Rd, Peria
37 |  | INCD-30440-F-TAU BLOCK | Moerewa 031372 - Tau Block |  | TAU BLOCK | 2025-04-30 09:05 | 45777.3785 | 2025-04-30 13:47 | 45777.5743 | 0.062486 | 0.00022158 | 8 | 2256 | Planned | Planned Outage | # Replace Poles, Clear Vegetation, Between Poles 424979 - 424993, McIntyre Rd, Moerewa
38 |  | INCD-30455-F-TAU BLOCK | Moerewa 031372 - Tau Block |  | TAU BLOCK | 2025-04-11 20:41 | 45758.862 | 2025-04-12 01:59 | 45759.0826 | 0.33322 | 0.0027421 | 99 | 12030.6 | Unplanned | Third Party | # Car vs Pole, Pole 340718, SH1, Moerewa
39 |  | INCD-30476-F-PUKEPOTO | Okahu CB1110 - Pukepoto |  | PUKEPOTO | 2025-04-13 11:56 | 45760.4971 | 2025-04-13 14:09 | 45760.5897 | 0.15081 | 0.0011356 | 41 | 5444.8 | Unplanned | Defective Equipment | # Replace Crossarm, Pole 413338, Okahu Rd, Kaitaia
40 |  | INCD-30476-F-REDAN ROAD | Okahu CB1107 - Redan Road |  | REDAN ROAD | 2025-04-13 11:56 | 45760.4971 | 2025-04-13 14:09 | 45760.5897 | 0.46163 | 0.0034622 | 125 | 16666.6667 | Unplanned | Defective Equipment | # Replace Crossarm, Pole 413338, Okahu Rd, Kaitaia
41 |  | INCD-30479-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-05-13 09:35 | 45790.3993 | 2025-05-13 15:42 | 45790.6542 | 0.33365 | 0.0031298 | 113 | 12046 | Planned | Planned Outage | # Replace Poles, Crossarms beyond Fuse F2265, Atwell Rd, Kaeo
42 |  | INCD-30482-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-04-14 16:55 | 45761.7048 | 2025-04-14 16:57 | 45761.7064 | 0.0048868 | 0.0021881 | 79 | 176.4333 | Unplanned | Defective Equipment | # Recloser Tripped, R1381, Far North Rd, Kauri Flat
43 |  | INCD-30491-F-TAU BLOCK | Moerewa 031372 - Tau Block |  | TAU BLOCK | 2025-05-16 09:24 | 45793.3917 | 2025-05-16 13:05 | 45793.5451 | 0.012242 | 5.5396e-05 | 2 | 442 | Planned | Planned Outage | # Relocate Pole 425001, SH1, Moerewa
44 |  | INCD-30494-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-05-21 09:40 | 45798.4028 | 2025-05-21 14:02 | 45798.5847 | 0.30479 | 0.0011633 | 42 | 11004 | Planned | Planned Outage | # Replace Pole at Transformer T01257, Poko Pohaia Rd, Kaitaia
45 |  | INCD-30500-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-04-15 09:30 | 45762.3958 | 2025-04-15 14:00 | 45762.5833 | 0.4508 | 0.0033791 | 122 | 16275.8167 | Planned | Planned Outage | # Planned Maintenance, Herekino Feeder, Okahu Rd, Kaitaia
46 |  | INCD-30500-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-04-15 09:30 | 45762.3958 | 2025-04-15 14:00 | 45762.5833 | 8.1965 | 0.061517 | 2221 | 295927.3833 | Planned | Planned Outage | # Planned Maintenance, Herekino Feeder, Okahu Rd, Kaitaia
47 |  | INCD-30503-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-04-15 10:01 | 45762.4174 | 2025-04-15 14:32 | 45762.6054 | 0.68255 | 0.0025205 | 91 | 24642.8 | Planned | Planned Outage | # Remove Redundant Equipment near Voltage Regulator VR13, Purerua Rd, Kerikeri
48 |  | INCD-30509-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-06-05 09:30 | 45813.3962 | 2025-06-06 17:30 | 45814.7292 | 1.0806 | 0.0029637 | 107 | 39014.6667 | Planned | Planned Outage | # Replace Recloser R460, SH12, Omapere
49 |  | INCD-30518-F-OXFORD STREET | Okahu CB1108 - Oxford Street |  | OXFORD STREET | 2025-05-16 09:30 | 45793.3958 | 2025-05-16 13:42 | 45793.5708 | 1.1639 | 0.0046187 | 166.7545 | 42022.1455 | Planned | Planned Outage | # Maintenance, Beyond Switch 007, Church Rd, Kaitaia
50 |  | INCD-30518-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-05-16 09:30 | 45793.3958 | 2025-05-16 13:42 | 45793.5708 | 0.37862 | 0.0015025 | 54.2455 | 13669.8545 | Planned | Planned Outage | # Maintenance, Beyond Switch 007, Church Rd, Kaitaia
51 |  | INCD-30524-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-05-28 09:30 | 45805.3958 | 2025-05-28 13:39 | 45805.5687 | 0.013793 | 5.5396e-05 | 2 | 498 | Planned | Planned Outage | # Remove Pole 417254, Matawera Rd, Kaitaia
52 |  | INCD-30542-F-TAU BLOCK | Moerewa 031372 - Tau Block |  | TAU BLOCK | 2025-05-07 10:34 | 45784.4403 | 2025-05-07 14:28 | 45784.6028 | 0.11666 | 0.00049856 | 18 | 4212 | Planned | Planned Outage | # Replace Pole 340718, SH1, Moerewa
53 |  | INCD-30548-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-04-16 11:44 | 45763.4888 | 2025-04-18 13:39 | 45765.5687 | 16.4395 | 0.037835 | 757 | 593530.3833 | Unplanned | Defective Equipment | # Cyclone Tam, Replace Insulator, King Bolt, Poles 428612, 410556, Far North Rd, Waimanoni
54 |  | INCD-30560-F-POKAPU | Moerewa 031312 - Pokapu |  | POKAPU | 2025-04-16 12:07 | 45763.505 | 2025-04-16 16:49 | 45763.7007 | 0.46334 | 0.0039331 | 142 | 16728.3 | Unplanned | Defective Equipment | # Cyclone Tam, Broken Insulator Clamp, Pole 425255, Pokapu Rd, Matawaia
55 |  | INCD-30584-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-04-16 13:44 | 45763.5722 | 2025-04-16 15:28 | 45763.6444 | 0.016009 | 0.00019388 | 6 | 578 | Unplanned | Unknown | # Cyclone Tam, Recloser R9001 Found Open, Iwitaua Rd, Mangamuka
56 |  | INCD-30605-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-04-16 14:45 | 45763.6146 | 2025-04-22 21:40 | 45769.9028 | 1.7887 | 0.00027674 | 3.9608 | 64579.4794 | Unplanned | Vegetation | # Cyclone Tam, Multiple Outages, South Road Feeder, Kaitaia
57 |  | INCD-30605-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2025-04-16 14:45 | 45763.6146 | 2025-04-22 21:40 | 45769.9028 | 6.3389 | 0.015636 | 223.785 | 228859.5014 | Unplanned | Vegetation | # Cyclone Tam, Multiple Outages, South Road Feeder, Kaitaia
58 |  | INCD-30605-F-SOUTH ROAD | Okahu CB1105 - South Road |  | SOUTH ROAD | 2025-04-16 14:45 | 45763.6146 | 2025-04-22 21:40 | 45769.9028 | 0.20228 | 0.0035422 | 50.6982 | 7303.1509 | Unplanned | Vegetation | # Cyclone Tam, Multiple Outages, South Road Feeder, Kaitaia
59 |  | INCD-30605-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-04-16 14:45 | 45763.6146 | 2025-04-22 21:40 | 45769.9028 | 2.553 | 0.00085789 | 12.2785 | 92174.165 | Unplanned | Vegetation | # Cyclone Tam, Multiple Outages, South Road Feeder, Kaitaia
60 |  | INCD-30605-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2025-04-16 14:45 | 45763.6146 | 2025-04-22 21:40 | 45769.9028 | 3.9135 | 0.0024076 | 34.4589 | 141292.862 | Unplanned | Vegetation | # Cyclone Tam, Multiple Outages, South Road Feeder, Kaitaia
61 |  | INCD-30605-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-04-16 14:45 | 45763.6146 | 2025-04-22 21:40 | 45769.9028 | 10.9664 | 0.011263 | 161.2044 | 395930.9718 | Unplanned | Vegetation | # Cyclone Tam, Multiple Outages, South Road Feeder, Kaitaia
62 |  | INCD-30605-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-04-16 14:45 | 45763.6146 | 2025-04-22 21:40 | 45769.9028 | 28.5097 | 0.062017 | 887.6143 | 1029315.3528 | Unplanned | Vegetation | # Cyclone Tam, Multiple Outages, South Road Feeder, Kaitaia
63 |  | INCD-30611-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-04-16 15:22 | 45763.6403 | 2025-04-24 16:22 | 45771.6819 | 35.153 | 0.032794 | 678 | 1269164.5333 | Unplanned | Adverse Weather | # Cyclone Tam, Adverse Weather Tripped R199, Russell Rd, Russell
64 |  | INCD-30614-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-04-16 15:25 | 45763.6422 | 2025-04-19 11:33 | 45766.4812 | 8.4378 | 0.088744 | 486 | 304636.95 | Unplanned | Defective Equipment | # Cyclone Tam, Crossarm Failure, Pole 440244, Ota Point Rd, Whangaroa
65 |  | INCD-30623-F-RIVERVIEW | Waipapa 041682 - Riverview |  | RIVERVIEW | 2025-04-16 15:40 | 45763.6528 | 2025-04-16 21:02 | 45763.8764 | 3.2893 | 0.034844 | 1258 | 118757.1 | Unplanned | Defective Equipment | # Cyclone Tam, Leaning Pole 417718, Landing Rd, Kerikeri
66 |  | INCD-30638-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-04-16 13:20 | 45763.5556 | 2025-04-16 17:47 | 45763.741 | 0.25144 | 0.00094172 | 34 | 9078 | Unplanned | Vegetation | # Cyclone Tam, Tree in Line, near Fuse F2048, Kimberley Rd, Te Kao
67 |  | INCD-30644-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-04-16 17:58 | 45763.7486 | 2025-04-16 19:53 | 45763.8285 | 0.076446 | 0.00066475 | 24 | 2760 | Unplanned | Vegetation | # Cyclone Tam, Tree on Line, near Transformer T03620, Te Rore Rd, Victoria Valley
68 |  | INCD-30665-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-04-16 18:28 | 45763.7692 | 2025-04-18 11:21 | 45765.4728 | 20.4801 | 0.023155 | 506 | 739413.9167 | Unplanned | Vegetation | # Cyclone Tam, Tree on Line, Pole 191782, Omaunu Rd, Kaeo
69 |  | INCD-30671-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-04-16 17:08 | 45763.7139 | 2025-04-18 19:20 | 45765.8056 | 30.2701 | 0.024873 | 605 | 1092871.3 | Unplanned | Vegetation | # Cyclone Tam, Vegetation Through Line, Pole 432411, 432375, Lamb Rd, Pukenui
70 |  | INCD-30683-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-04-16 06:35 | 45763.2743 | 2025-04-20 16:20 | 45767.6806 | 0.65149 | 0.00016912 | 4.7507 | 23521.3064 | Unplanned | Vegetation | # Cyclone Tam, Tree Contact with Line, Beyond Recloser R363, Barriball Rd, Oruru
71 |  | INCD-30683-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-04-16 06:35 | 45763.2743 | 2025-04-20 16:20 | 45767.6806 | 81.9683 | 0.042762 | 1201.2493 | 2959383.2103 | Unplanned | Vegetation | # Cyclone Tam, Tree Contact with Line, Beyond Recloser R363, Barriball Rd, Oruru
72 |  | INCD-30695-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2025-04-16 20:11 | 45763.8407 | 2025-04-17 11:55 | 45764.4967 | 35.143 | 0.040716 | 1414.4154 | 1268802.35 | Unplanned | Vegetation | # Cyclone Tam, Replace Cross arm, Pole 404073, Aucks Rd, Okiato
73 |  | INCD-30695-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2025-04-16 20:11 | 45763.8407 | 2025-04-17 11:55 | 45764.4967 | 5.6239 | 0.0068967 | 239.5846 | 203047.05 | Unplanned | Vegetation | # Cyclone Tam, Replace Cross arm, Pole 404073, Aucks Rd, Okiato
74 |  | INCD-30704-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-04-15 18:31 | 45762.7715 | 2025-04-22 17:27 | 45769.7271 | 54.9215 | 0.17591 | 1348.8937 | 1982887.1833 | Unplanned | Defective Equipment | # Cyclone Tam, Binder Failed on Conductor, Oruru Rd, Tokerau
75 |  | INCD-30704-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-04-15 18:31 | 45762.7715 | 2025-04-22 17:27 | 45769.7271 | 0.061283 | 0.0015788 | 12.1063 | 2212.55 | Unplanned | Defective Equipment | # Cyclone Tam, Binder Failed on Conductor, Oruru Rd, Tokerau
76 |  | INCD-30731-F-ONEWHERO | Haruru CB0608 - Onewhero |  | ONEWHERO | 2025-04-16 21:14 | 45763.8847 | 2025-04-17 14:27 | 45764.6021 | 0.21285 | 0.00083449 | 14.0086 | 7684.6715 | Unplanned | Defective Equipment | # Cyclone Tam, Cable Fault, near Fuse F_T02003, Puketona Rd, Paihia
77 |  | INCD-30731-F-TI BAY | Haruru CB0606 - Ti Bay |  | TI BAY | 2025-04-16 21:14 | 45763.8847 | 2025-04-17 14:27 | 45764.6021 | 15.5688 | 0.044618 | 748.9914 | 562094.1619 | Unplanned | Defective Equipment | # Cyclone Tam, Cable Fault, near Fuse F_T02003, Puketona Rd, Paihia
78 |  | INCD-30740-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-04-16 21:33 | 45763.8981 | 2025-04-17 14:36 | 45764.6082 | 18.7214 | 0.018308 | 661 | 675916.5667 | Unplanned | Adverse Weather | # Cyclone Tam, 33kV Line Tripped, Church Rd, Kaitaia
79 |  | INCD-30752-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-04-16 21:46 | 45763.907 | 2025-04-19 17:08 | 45766.7137 | 12.0268 | 0.010497 | 284 | 434216.1833 | Unplanned | Defective Equipment | # Cyclone Tam, Replace Crossarm, Pole 332387, Waiare Rd, Puketi
80 |  | INCD-30794-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-04-16 23:44 | 45763.9889 | 2025-04-18 11:05 | 45765.4618 | 6.2994 | 0.0077831 | 281 | 227434 | Unplanned | Vegetation | # Cyclone Tam, Vegetation on Line beyond S064, Waipapa
81 |  | INCD-30815-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-04-16 18:08 | 45763.7555 | 2025-04-19 11:14 | 45766.4681 | 22.7356 | 0.015428 | 539.0323 | 820846.2333 | Unplanned | Vegetation | # Cyclone Tam, Multiple Faults Kaikohe Feeder, Umawera
82 |  | INCD-30815-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-04-16 18:08 | 45763.7555 | 2025-04-19 11:14 | 45766.4681 | 0.065147 | 2.7698e-05 | 0.96774 | 2352.05 | Unplanned | Vegetation | # Cyclone Tam, Multiple Faults Kaikohe Feeder, Umawera
83 |  | INCD-30842-F-KAIKOHE | Kaikohe CB0107 - Kaikohe |  | KAIKOHE | 2025-04-17 01:09 | 45764.0481 | 2025-04-18 11:59 | 45765.4993 | 8.1915 | 0.067527 | 1248 | 295745.7667 | Unplanned | Vegetation | # Cyclone Tam, Repair Conductor, near Pole 413994, Taheke Rd, Kaikohe
84 |  | INCD-30854-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-04-16 16:06 | 45763.6708 | 2025-04-19 15:06 | 45766.6292 | 13.2453 | 0.007423 | 268 | 478208.2833 | Unplanned | Vegetation | # Cyclone Tam, Tree Contact, Line Down, SH1, Towai
85 |  | INCD-30872-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-04-17 00:46 | 45764.0319 | 2025-04-17 14:40 | 45764.6111 | 8.9407 | 0.012104 | 437 | 322796.5167 | Unplanned | Adverse Weather | # Cyclone Tam, Circuit Breaker Tripped 051772, SH12, Omanaia
86 |  | INCD-30881-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-04-17 01:56 | 45764.0806 | 2025-04-17 11:03 | 45764.4605 | 7.2538 | 0.013683 | 494 | 261892.85 | Unplanned | Adverse Weather | # Cyclone Tam, Recloser Tripped R694, Settlers Way, Okaihau
87 |  | INCD-30893-F-OMAUNU ROAD | Kaeo 191712 - Omaunu Rd |  | OMAUNU ROAD | 2025-04-17 02:05 | 45764.0867 | 2025-04-17 12:46 | 45764.5321 | 2.0251 | 0.0031575 | 114 | 73113.9 | Unplanned | Adverse Weather | # Cyclone Tam, Circuit Breaker CB1712 Tripped, Omaunu Rd, Kaeo
88 |  | INCD-30893-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-04-17 02:05 | 45764.0867 | 2025-04-17 12:46 | 45764.5321 | 0.37304 | 0.00058165 | 21 | 13468.35 | Unplanned | Adverse Weather | # Cyclone Tam, Circuit Breaker CB1712 Tripped, Omaunu Rd, Kaeo
89 |  | INCD-30911-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-04-17 03:05 | 45764.1282 | 2025-04-21 16:35 | 45768.691 | 3.9495 | 0.0039885 | 144 | 142592.8333 | Unplanned | Adverse Weather | # Cyclone Tam, Multiple Faults, SH1, Pakaraka, Kaikohe
90 |  | INCD-30914-F-KAWAKAWA | Kawakawa CB0207 - Kawakawa |  | KAWAKAWA | 2025-04-17 03:32 | 45764.1475 | 2025-04-17 21:58 | 45764.9152 | 0.68677 | 0.0015788 | 57 | 24795 | Unplanned | Vegetation | # Cyclone Tam, Poles 402585, 912371, Down dute to Vegetation, Kawakawa
91 |  | INCD-30914-F-KARETU | Kawakawa CB0210 - Karetu |  | KARETU | 2025-04-17 03:32 | 45764.1475 | 2025-04-17 21:58 | 45764.9152 | 0.0071165 | 0.0052072 | 188 | 256.9333 | Unplanned | Vegetation | # Cyclone Tam, Poles 402585, 912371, Down dute to Vegetation, Kawakawa
92 |  | INCD-30914-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2025-04-17 03:32 | 45764.1475 | 2025-04-17 21:58 | 45764.9152 | 12.2086 | 0.037503 | 1354 | 440780.7167 | Unplanned | Vegetation | # Cyclone Tam, Poles 402585, 912371, Down dute to Vegetation, Kawakawa
93 |  | INCD-30923-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-04-17 04:39 | 45764.1935 | 2025-04-20 10:26 | 45767.4347 | 0.96518 | 0.00022158 | 8 | 34847 | Unplanned | Adverse Weather | # Cyclone Tam, Multiple Outages, SH10, Mt Pokaka
94 |  | INCD-30923-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2025-04-17 04:39 | 45764.1935 | 2025-04-20 10:26 | 45767.4347 | 11.0247 | 0.020552 | 742 | 398034.85 | Unplanned | Adverse Weather | # Cyclone Tam, Multiple Outages, SH10, Mt Pokaka
95 |  | INCD-30938-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-04-17 07:26 | 45764.3099 | 2025-04-18 18:34 | 45765.7736 | 3.7959 | 0.0025205 | 91 | 137046.6 | Unplanned | Defective Equipment | # Cyclone Tam, Crossarm Failure, Pole 416732, Rangihoua Rd, Purerua
96 |  | INCD-30947-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-04-17 08:00 | 45764.3331 | 2025-04-17 20:00 | 45764.8331 | 3.1725 | 0.014184 | 492.6648 | 114538.3812 | Unplanned | Vegetation | # Cyclone Tam, 33kV Line Tripped CB043352 due to Tree, Waipapa Loop Rd, Kaitaia
97 |  | INCD-30947-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-04-17 08:00 | 45764.3331 | 2025-04-17 20:00 | 45764.8331 | 15.4441 | 0.069686 | 2420.4236 | 557592.7322 | Unplanned | Vegetation | # Cyclone Tam, 33kV Line Tripped CB043352 due to Tree, Waipapa Loop Rd, Kaitaia
98 |  | INCD-30947-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-04-17 08:00 | 45764.3331 | 2025-04-17 20:00 | 45764.8331 | 5.3513 | 0.017531 | 608.9116 | 193202.2699 | Unplanned | Vegetation | # Cyclone Tam, 33kV Line Tripped CB043352 due to Tree, Waipapa Loop Rd, Kaitaia
99 |  | INCD-30953-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-04-16 14:32 | 45763.6059 | 2025-04-19 13:31 | 45766.5632 | 7.877 | 0.018724 | 425 | 284389.9333 | Unplanned | Vegetation | # Cyclone Tam, Tree in Line, Pole 434114, Mangakahia Rd, Awarua
100 |  | INCD-30998-F-KAWAKAWA | Kawakawa CB0207 - Kawakawa |  | KAWAKAWA | 2025-04-17 11:34 | 45764.4819 | 2025-04-17 11:50 | 45764.4931 | 0.054509 | 0.0034068 | 123 | 1968 | Unplanned | Adverse Weather | # Cyclone Tam, Fuse 1737 Found Open, Church Street, Kawakawa
101 |  | INCD-31229-F-MOEREWA | Moerewa 031322 - Moerewa |  | MOEREWA | 2025-04-17 16:42 | 45764.6961 | 2025-04-18 02:13 | 45765.0924 | 1.0554 | 0.0053734 | 194 | 38103.5167 | Unplanned | Unknown | # Cyclone Tam, Recloser R565 Tripped, SH1, Moerewa
102 |  | INCD-31277-F-KERIKERI ROAD | Kerikeri 181112 - Kerikeri Road |  | KERIKERI ROAD | 2025-04-16 12:26 | 45763.5178 | 2025-04-18 02:09 | 45765.0896 | 2.6147 | 0.028169 | 858.4638 | 94401.7333 | Unplanned | Defective Equipment | # Cyclone Tam, Wires Down Beyond Fuse F2238, Riddell Rd, Kerikeri
103 |  | INCD-31277-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2025-04-16 12:26 | 45763.5178 | 2025-04-18 02:09 | 45765.0896 | 2.6699 | 0.014652 | 446.5362 | 96395.2 | Unplanned | Defective Equipment | # Cyclone Tam, Wires Down Beyond Fuse F2238, Riddell Rd, Kerikeri
104 |  | INCD-31466-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-04-18 08:20 | 45765.3472 | 2025-04-18 17:02 | 45765.7097 | 2.5157 | 0.0048194 | 174 | 90828 | Unplanned | Adverse Weather | # Conductor Off Pole 422451, Far North Rd, Pukenui
105 |  | INCD-31580-F-OMAUNU ROAD | Kaeo 191712 - Omaunu Rd |  | OMAUNU ROAD | 2025-04-18 11:00 | 45765.4585 | 2025-04-18 17:03 | 45765.7107 | 1.1957 | 0.0063428 | 229 | 43170.95 | Unplanned | Defective Equipment | # Cyclone Tam, Reattach Jumper to Fuse L814, Omaunu Rd, Kaeo
106 |  | INCD-31580-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-04-18 11:00 | 45765.4585 | 2025-04-18 17:03 | 45765.7107 | 0.067656 | 0.0011633 | 42 | 2442.65 | Unplanned | Defective Equipment | # Cyclone Tam, Reattach Jumper to Fuse L814, Omaunu Rd, Kaeo
107 |  | INCD-31631-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-04-18 11:58 | 45765.4988 | 2025-04-19 12:55 | 45766.5382 | 0.92643 | 0.0049025 | 177 | 33447.8 | Unplanned | Defective Equipment | # Cyclone Tam, Flipped Crossarm, Pole 426871, Cable Bay Block Rd, Coopers Beach
108 |  | INCD-31643-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-04-18 12:31 | 45765.5215 | 2025-04-18 12:50 | 45765.5347 | 0.0036838 | 0.00019388 | 7 | 133 | Unplanned | Vegetation | # Cyclone Tam, Tree in Line, at Pole 411469, Saward Rd, Omapere
109 |  | INCD-31676-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-04-17 10:41 | 45764.4451 | 2025-04-19 16:34 | 45766.6903 | 20.0139 | 0.010968 | 396 | 722582.5333 | Unplanned | Defective Equipment | # Cyclone Tam, Repair Line, Beyond Fuse F2071, Okaka Rd, Utakura
110 |  | INCD-31694-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-04-16 10:20 | 45763.4308 | 2025-04-22 14:43 | 45769.6132 | 20.1619 | 0.094172 | 1110.9481 | 727924.1 | Unplanned | Vegetation | # Cyclone Tam, Multiple Faults, Opononi Feeder
111 |  | INCD-31694-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-04-16 10:20 | 45763.4308 | 2025-04-22 14:43 | 45769.6132 | 0.0064767 | 5.5396e-05 | 0.6535 | 233.8333 | Unplanned | Vegetation | # Cyclone Tam, Multiple Faults, Opononi Feeder
112 |  | INCD-31694-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-04-16 10:20 | 45763.4308 | 2025-04-22 14:43 | 45769.6132 | 1.0169 | 0.0039331 | 46.3984 | 36714.6167 | Unplanned | Vegetation | # Cyclone Tam, Multiple Faults, Opononi Feeder
113 |  | INCD-31736-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-04-18 12:19 | 45765.5132 | 2025-04-21 14:04 | 45768.5861 | 0.4335 | 0.00058165 | 21 | 15651 | Unplanned | Defective Equipment | # Cyclone Tam, Tails to Fuse Bases Blown Off, F_T04614, Waiare Rd, Waipapa
114 |  | INCD-31832-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-04-16 14:45 | 45763.6146 | 2025-04-20 19:09 | 45767.7979 | 0.16424 | 0.00023169 | 1.8588 | 5929.6122 | Unplanned | Vegetation | # Cyclone Tam, Trees on Lines, Poles, Beyond Fuse F2072, Pukemiro Rd, Broadwood
115 |  | INCD-31832-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2025-04-16 14:45 | 45763.6146 | 2025-04-20 19:09 | 45767.7979 | 0.00038522 | 5.7412e-06 | 0.046062 | 13.9079 | Unplanned | Vegetation | # Cyclone Tam, Trees on Lines, Poles, Beyond Fuse F2072, Pukemiro Rd, Broadwood
116 |  | INCD-31832-F-SOUTH ROAD | Okahu CB1105 - South Road |  | SOUTH ROAD | 2025-04-16 14:45 | 45763.6146 | 2025-04-20 19:09 | 45767.7979 | 0.00079529 | 1.1853e-05 | 0.095097 | 28.7132 | Unplanned | Vegetation | # Cyclone Tam, Trees on Lines, Poles, Beyond Fuse F2072, Pukemiro Rd, Broadwood
117 |  | INCD-31862-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-04-17 06:55 | 45764.2882 | 2025-04-19 17:30 | 45766.7292 | 0.87622 | 0.00024928 | 9 | 31635 | Unplanned | Adverse Weather | # Cyclone Tam, Replace Blown Fuse F2104, Stanners Rd, Waipapa
118 |  | INCD-31865-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2025-04-18 07:45 | 45765.3229 | 2025-04-19 17:31 | 45766.7299 | 0.28058 | 0.00013849 | 5 | 10130 | Unplanned | Adverse Weather | # Cyclone Tam, Replace Blown Fuse F2178, Omapere Rd, Kaikohe
119 |  | INCD-31877-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-04-18 07:37 | 45765.3174 | 2025-04-20 16:42 | 45767.6958 | 3.8993 | 0.0012187 | 44 | 140779 | Unplanned | Defective Equipment | # Cyclone Tam, Repair Jumper, at Pole 211773, Waiotemarama Gorge Rd, Omanaia
120 |  | INCD-32024-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-04-20 15:28 | 45767.6441 | 2025-04-20 17:02 | 45767.71 | 0.23103 | 0.0024374 | 88 | 8340.9333 | Unplanned | Defective Equipment | # Cyclone Tam, Fix Crossarm, Pole 416913, Purerua Rd, Waipapa
121 |  | INCD-32036-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2025-04-21 09:46 | 45768.4069 | 2025-04-21 11:10 | 45768.4653 | 0.016286 | 0.00019388 | 7 | 588 | Unplanned | Defective Equipment | # Cyclone Tam, Broken Wire, Near Link L280, SH10, Kaeo
122 |  | INCD-32045-F-ONEWHERO | Haruru CB0608 - Onewhero |  | ONEWHERO | 2025-04-21 16:18 | 45768.6792 | 2025-04-21 21:45 | 45768.9062 | 0.42114 | 0.0029083 | 105 | 15205 | Unplanned | Defective Equipment | # Cyclone Tam, Conductor Dropped near Cows, Pole 408270, Haruru Falls Rd, Haruru
123 |  | INCD-32051-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-04-21 14:11 | 45768.591 | 2025-04-21 18:31 | 45768.7715 | 2.1316 | 0.0081985 | 296 | 76960 | Unplanned | Vegetation | # Cyclone Tam, Line Down Near Pole 408718, SH10, Totara North, Kaeo
124 |  | INCD-32060-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-04-22 14:27 | 45769.6024 | 2025-04-22 18:11 | 45769.7577 | 0.19818 | 0.00088633 | 32 | 7155.2 | Unplanned | Defective Equipment | # Cyclone Tam, Wire Off Insulator, at Pole 145283, Windy Hill Rd, Lower Waihou
125 |  | INCD-32072-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-04-22 15:09 | 45769.6312 | 2025-04-22 18:56 | 45769.789 | 2.3643 | 0.013683 | 494 | 85361.55 | Unplanned | Defective Equipment | # Cyclone Tam, Broken Suspension Clamp, at Pole 419663, Cook Rd, Okaihau
126 |  | INCD-32117-F-PUKETONA | Haruru CB0607 - Puketona |  | PUKETONA | 2025-05-28 09:02 | 45805.3764 | 2025-05-28 14:32 | 45805.6056 | 0.41541 | 0.0018834 | 68 | 14998 | Planned | Planned Outage | # Replace Fuses and Crossarms at Transformer T04783, Puketutu Rd, Haruru
127 |  | INCD-32120-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2025-05-20 09:33 | 45797.3979 | 2025-05-20 15:33 | 45797.6479 | 1.7412 | 0.0054288 | 196 | 62865 | Planned | Planned Outage | # Install New Links, at Pole 427571, North Road, Kaitaia
128 |  | INCD-32123-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-05-23 09:42 | 45800.4042 | 2025-05-23 13:30 | 45800.5625 | 0.044206 | 0.00019388 | 7 | 1596 | Planned | Planned Outage | # Replace Crossarms, on Poles 424572, Taemaro Rd, Taipa
129 |  | INCD-32132-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-05-27 09:38 | 45804.4014 | 2025-05-27 12:23 | 45804.516 | 0.050271 | 0.00030468 | 11 | 1815 | Planned | Planned Outage | # Install Pole at Transformer T02922, Sweetwater Rd, Kaitaia
130 |  | INCD-32144-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-06-09 09:36 | 45817.4 | 2025-06-09 12:18 | 45817.5125 | 0.20192 | 0.0012464 | 45 | 7290 | Planned | Planned Outage | # Relocate SWER from temporary Pole to Original Pole 414568, West Coast Rd, Panguru
131 |  | INCD-32147-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-04-26 16:13 | 45773.6757 | 2025-04-26 18:10 | 45773.7569 | 0.025787 | 0.00052626 | 19 | 931 | Unplanned | Defective Equipment | # Defective Crossarm, Pole 431195, SH1, Ohaeawai
132 |  | INCD-32156-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-04-28 12:44 | 45775.5304 | 2025-04-28 17:14 | 45775.7181 | 0.90987 | 0.0098327 | 355 | 32850.0333 | Unplanned | Vegetation | # SWER Conductor Down Beyond R_T02152, Manawaora Rd, Russell
133 |  | INCD-32165-F-PUKETONA | Haruru CB0607 - Puketona |  | PUKETONA | 2025-05-02 09:02 | 45779.3764 | 2025-05-02 13:07 | 45779.5465 | 0.088217 | 0.00036007 | 13 | 3185 | Planned | Planned Outage | # Replace Poles 438199, 438240, Puketona Rd, Haruru
134 |  | INCD-32168-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-05-07 09:14 | 45784.3847 | 2025-05-07 15:36 | 45784.65 | 0.23704 | 0.00080324 | 29 | 8558 | Planned | Planned Outage | # Replace Pole, Transformer T04183, Signal Rd, Waipapa
135 |  | INCD-32174-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-04-29 08:17 | 45776.3451 | 2025-04-30 13:58 | 45777.5819 | 0.3619 | 0.00038777 | 14 | 13066 | Unplanned | Defective Equipment | # Defective Pole 43808 Down, Motukiore Rd, Kaikohe
136 |  | INCD-32186-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-04-30 09:33 | 45777.3979 | 2025-04-30 11:01 | 45777.459 | 0.029249 | 0.00033237 | 12 | 1056 | Unplanned | Vegetation | # Removed Large Tree from Conductor, Beyond Fuse F2035, Trig Rd, Pukenui
137 |  | INCD-32195-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-04-30 14:02 | 45777.5851 | 2025-04-30 14:14 | 45777.5934 | 0.031156 | 0.0026036 | 94 | 1124.8667 | Unplanned | Defective Equipment | # Defective Crossarm, Pole 419069, SH10, Lake Ohia
138 |  | INCD-32204-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-04-30 18:15 | 45777.7604 | 2025-04-30 22:11 | 45777.9243 | 0.62098 | 0.0026313 | 95 | 22420 | Unplanned | Defective Equipment | # Defective Cable Termination, Transformer T03823, Onekura Rd, Pungarere
139 |  | INCD-32207-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-04-30 18:15 | 45777.7604 | 2025-05-01 10:53 | 45778.4535 | 2.5524 | 0.0052626 | 95 | 92153 | Unplanned | Vegetation | # Tree in Line, at Pole 406932, Onekura Rd, Pungarere
140 |  | INCD-32210-F-OMAUNU ROAD | Kaeo 191712 - Omaunu Rd |  | OMAUNU ROAD | 2025-05-23 10:17 | 45800.4285 | 2025-05-23 16:56 | 45800.7056 | 0.28734 | 0.00072014 | 26 | 10374 | Planned | Planned Outage | # Replace Pole 410110, Matawherohia Rd, Kaeo
141 |  | INCD-32216-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-05-01 11:15 | 45778.4688 | 2025-05-01 12:37 | 45778.5257 | 0.054509 | 0.00066475 | 24 | 1968 | Unplanned | Defective Equipment | # Low Conductor Spans, Pole 407157, Te Rore Rd, Okahu Rd
142 |  | INCD-32234-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-05-14 10:37 | 45791.4424 | 2025-05-14 13:54 | 45791.5792 | 0.0039054 | 2.7698e-05 | 0.92593 | 141 | Planned | Planned Outage | # Replace Pole 412871, SH1, Mangamuka Bridge, Kaikohe
143 |  | INCD-32234-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-05-14 10:37 | 45791.4424 | 2025-05-14 13:54 | 45791.5792 | 0.77717 | 0.005955 | 199.0741 | 28059 | Planned | Planned Outage | # Replace Pole 412871, SH1, Mangamuka Bridge, Kaikohe
144 |  | INCD-32240-F-RIVERVIEW | Waipapa 041682 - Riverview |  | RIVERVIEW | 2025-05-18 09:31 | 45795.3965 | 2025-05-18 13:17 | 45795.5535 | 2.0594 | 0.0091126 | 329 | 74354 | Planned | Planned Outage | # Replace Pole 417718, Landing Rd, Waipapa
145 |  | INCD-32246-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-05-04 10:10 | 45781.4236 | 2025-05-04 13:49 | 45781.5757 | 0.042461 | 0.00019388 | 7 | 1533 | Unplanned | Defective Equipment | # Flipped Crossarm, at Pole 435676, Rarawa Beach Rd, Pukenui
146 |  | INCD-32249-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-05-22 10:01 | 45799.4174 | 2025-05-22 13:25 | 45799.559 | 0.02177 | 0.00011079 | 4 | 786 | Planned | Planned Outage | # Replace Crossarm on Pole 318689, SH12, Rawene
147 |  | INCD-32261-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-05-27 09:05 | 45804.3785 | 2025-05-27 14:37 | 45804.609 | 0.10425 | 0.00033237 | 12 | 3764 | Planned | Planned Outage | # Pole Replacement, at L627, Takahe Rd, Waipapa
148 |  | INCD-32264-F-TAU BLOCK | Moerewa 031372 - Tau Block |  | TAU BLOCK | 2025-05-28 09:00 | 45805.375 | 2025-05-28 13:56 | 45805.5806 | 0.06437 | 0.00074784 | 19 | 2324 | Planned | Planned Outage | # Replace Pole, beyond L876, McIntyre Rd, Moerewa
149 |  | INCD-32267-F-MATAURI BAY | Kaeo 191732 - Matauri Bay |  | MATAURI BAY | 2025-06-12 10:06 | 45820.4208 | 2025-06-12 14:29 | 45820.6035 | 0.029138 | 0.00011079 | 4 | 1052 | Planned | Planned Outage | # Install Voltage Regulator VR20, Wainui Rd, Kaeo
150 |  | INCD-32273-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-05-05 20:35 | 45782.8576 | 2025-05-06 12:35 | 45783.5243 | 0.20858 | 0.0014957 | 54 | 7530.4667 | Unplanned | Unknown | # Failed Insulator, at Pole 405616, SH12, Omanaia
151 |  | INCD-32273-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-05-05 20:35 | 45782.8576 | 2025-05-06 12:35 | 45783.5243 | 0.012409 | 5.5396e-05 | 2 | 448 | Unplanned | Unknown | # Failed Insulator, at Pole 405616, SH12, Omanaia
152 |  | INCD-32279-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-05-06 09:43 | 45783.4049 | 2025-05-06 14:36 | 45783.6083 | 0.20289 | 0.00069244 | 25 | 7325 | Unplanned | Planned Outage | # Pole Replacement, Beyond Switch 351, Kaitaia Awaroa Rd, Kaitaia
153 |  | INCD-32288-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-05-28 09:32 | 45805.3972 | 2025-05-28 15:27 | 45805.6438 | 0.078551 | 0.00022158 | 8 | 2836 | Planned | Planned Outage | # Replace Pole 436947, Wainui Rd, Whangaroa
154 |  | INCD-32291-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2025-05-28 22:32 | 45805.9389 | 2025-05-29 04:09 | 45806.1729 | 0.018668 | 5.5396e-05 | 2 | 674 | Planned | Planned Outage | # Replace Pole 403043, Oromahoe Rd, Kawakawa
155 |  | INCD-32297-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-05-07 10:19 | 45784.4299 | 2025-05-07 13:18 | 45784.5542 | 0.014209 | 8.3093e-05 | 3 | 513 | Unplanned | Defective Equipment | # Replace Transformer T05125, Tracey Rd, Kaikohe
156 |  | INCD-32303-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-05-30 09:01 | 45807.3757 | 2025-05-30 11:13 | 45807.4673 | 0.21181 | 0.0016065 | 58 | 7647.3 | Planned | Planned Outage | # Replace Insulators, at Recloser R587, Te Pua Rd, Kaikohe
157 |  | INCD-32309-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-06-03 09:33 | 45811.3979 | 2025-06-03 13:06 | 45811.5458 | 0.34218 | 0.0016065 | 58 | 12354 | Planned | Planned Outage | # Replace Poles 417973 to 417977, Taronui Rd, Waipapa
158 |  | INCD-32315-F-PUKETONA | Haruru CB0607 - Puketona |  | PUKETONA | 2025-06-05 09:03 | 45813.3771 | 2025-06-05 12:15 | 45813.5104 | 0.069134 | 0.00036007 | 13 | 2496 | Planned | Planned Outage | # Replace Pole 438240, Puketona Rd, Haruru
159 |  | INCD-32321-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-05-08 19:57 | 45785.8313 | 2025-05-09 11:23 | 45786.4743 | 0.89768 | 0.00096942 | 35 | 32410 | Unplanned | Defective Equipment | # Broken Conductor Between Poles 419364 and 419367, Honeymoon Valley Rd, Taipa
160 |  | INCD-32324-F-AERODROME ROAD | Waipapa 041622 - Aerodrome Rd |  | AERODROME ROAD | 2025-05-21 08:30 | 45798.3542 | 2025-05-22 15:02 | 45799.6264 | 0.050742 | 2.7698e-05 | 1 | 1832 | Planned | Planned Outage | # Install Ring Main Unit RM286, Kaihikatearoa Lane Extension, Waipapa
161 |  | INCD-32345-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-05-10 01:08 | 45787.0471 | 2025-05-10 01:34 | 45787.065 | 0.061964 | 0.0025482 | 92 | 2237.1333 | Unplanned | Wildlife | # Possum Damage, at Recloser R050, Callaghan Rd, Kawakawa
162 |  | INCD-32366-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-06-10 09:33 | 45818.3979 | 2025-06-10 10:07 | 45818.4214 | 0.33852 | 0.039552 | 1428 | 12222 | Planned | Planned Outage | # Upgrade Transformer T09299, Tokerau Beach Rd, Karikari Peninsula
163 |  | INCD-32369-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2025-06-12 09:37 | 45820.4007 | 2025-06-12 15:20 | 45820.6389 | 0.31916 | 0.00099712 | 36 | 11523 | Planned | Planned Outage | # Replace Pole 436399, Upgrade Transformer T04529, Montrose Rd, Kerikeri
164 |  | INCD-32384-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-06-25 10:12 | 45833.425 | 2025-06-25 16:39 | 45833.6937 | 1.0646 | 0.0031021 | 112 | 38436 | Planned | Planned Outage | # Replace Crossarms, Earthbank at R_T09124, Rawhiti Rd, Kawakawa
165 |  | INCD-32387-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2026-01-14 09:33 | 46036.3979 | 2026-01-14 15:04 | 46036.6278 | 0.28421 | 0.00085863 | 31 | 10261 | Planned | Planned Outage | # Replace Poles, Crossarms beyond Switch 167, Wharekawa Rd, Omanaia
166 |  | INCD-32444-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2026-02-04 10:04 | 46057.4194 | 2026-02-04 15:21 | 46057.6396 | 0.035121 | 0.00011079 | 4 | 1268 | Planned | Planned Outage | # Replace Poles, Beyond L580, Wharekawa Rd, Omanaia
167 |  | INCD-32456-F-SOUTH ROAD | Okahu CB1105 - South Road |  | SOUTH ROAD | 2025-04-19 15:38 | 45766.6515 | 2025-04-19 15:43 | 45766.6548 | 0.00849 | 0.0017749 | 64.0815 | 306.5233 | Unplanned | Defective Equipment | # Replace T01279, Beyond L762, Fryer Rd, Kaitaia
168 |  | INCD-32456-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2025-04-19 15:38 | 45766.6515 | 2025-04-19 15:43 | 45766.6548 | 0.0041123 | 0.00085972 | 31.0395 | 148.4722 | Unplanned | Defective Equipment | # Replace T01279, Beyond L762, Fryer Rd, Kaitaia
169 |  | INCD-32456-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-04-19 15:38 | 45766.6515 | 2025-04-19 15:43 | 45766.6548 | 0.091533 | 0.019136 | 690.879 | 3304.7045 | Unplanned | Defective Equipment | # Replace T01279, Beyond L762, Fryer Rd, Kaitaia
170 |  | INCD-32459-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-05-13 12:15 | 45790.5104 | 2025-05-13 14:23 | 45790.5993 | 0.20208 | 0.0015788 | 57 | 7296 | Unplanned | Defective Equipment | # Replace Kingbolt at Pole 421067, Parapara Rd, Taipa
171 |  | INCD-32471-F-PUKEPOTO | Okahu CB1110 - Pukepoto |  | PUKEPOTO | 2025-06-30 09:32 | 45838.3972 | 2025-06-30 12:37 | 45838.5257 | 0.035869 | 0.00019388 | 7 | 1295 | Planned | Planned Outage | # Replace Pole 413471 at Transformer T20093, Bonnett Rd, Kaitaia
172 |  | INCD-32480-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-05-14 15:19 | 45791.6382 | 2025-05-14 19:01 | 45791.7924 | 0.33204 | 0.0014957 | 54 | 11988 | Planned | Planned Outage | # Reconnect Jumpers at Pole 422367, Kohukohu Rd, Kaitaia
173 |  | INCD-32480-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-05-14 15:19 | 45791.6382 | 2025-05-14 19:01 | 45791.7924 | 0.0061489 | 2.7698e-05 | 1 | 222 | Planned | Planned Outage | # Reconnect Jumpers at Pole 422367, Kohukohu Rd, Kaitaia
174 |  | INCD-32483-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-06-18 22:30 | 45826.9376 | 2025-06-19 03:11 | 45827.1325 | 1.2825 | 0.0045701 | 165 | 46304.5 | Planned | Planned Outage | # Maintenance on Switch 232, Replace Crossarms, SH10, Taipa
175 |  | INCD-32492-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-05-21 09:13 | 45798.384 | 2025-05-21 14:01 | 45798.584 | 0.11168 | 0.00038777 | 14 | 4032 | Planned | Planned Outage | # Replace Transformer, Crossarms, Poles at T01582, Cumber Rd, Kaikohe
176 |  | INCD-32510-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-05-16 23:15 | 45793.9688 | 2025-05-16 23:39 | 45793.9854 | 0.0039885 | 0.00016619 | 6 | 144 | Unplanned | Defective Equipment | # Replace Joint, at Fuse F2177, Te Waiarohia Rd, Omanaia
177 |  | INCD-32531-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-06-10 09:01 | 45818.3757 | 2025-06-10 15:12 | 45818.6333 | 0.071931 | 0.00019388 | 7 | 2597 | Planned | Planned Outage | # Vegetation Control, Turk Valley Rd, Pukenui
178 |  | INCD-32543-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2025-05-20 17:06 | 45797.7128 | 2025-05-20 20:04 | 45797.8361 | 0.7649 | 0.015926 | 575 | 27616.0833 | Unplanned | Defective Equipment | # Faulty Cable cut from Overhead at Pole 427525, Donald Lane, Kaitaia
179 |  | INCD-32561-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-06-17 11:01 | 45825.459 | 2025-06-17 15:21 | 45825.6396 | 0.014403 | 5.5396e-05 | 2 | 520 | Planned | Planned Outage | # Install Transformer T20089, SH10, WAIPAPA
180 |  | INCD-32567-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-06-24 09:34 | 45832.3985 | 2025-06-24 15:20 | 45832.6388 | 1.9456 | 0.0056503 | 204 | 70244 | Planned | Planned Outage | # Replace Poles, Crossarms, Beyond Switch 351, Kaitaia-Awaroa Rd, Herekino
181 |  | INCD-32576-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-06-26 09:07 | 45834.3799 | 2025-06-26 15:41 | 45834.6535 | 2.1077 | 0.0056503 | 204 | 76097.6667 | Planned | Planned Outage | # Replace Poles, Crossarms, Between Switch 351, Sectionaliser S1006., Awaroa Rd, Herekino
182 |  | INCD-32579-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-07-01 09:32 | 45839.3972 | 2025-07-01 15:21 | 45839.6398 | 0.25962 | 0.0057057 | 206 | 9373.5 | Planned | Planned Outage | # Replace Poles Between Switch 351 and Sectionaliser S1006, Awaroa Rd, Herekino
183 |  | INCD-32594-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-05-26 13:16 | 45803.5528 | 2025-05-26 19:48 | 45803.825 | 0.64597 | 0.0072845 | 263 | 23322.2167 | Unplanned | Third Party | # Tractor vs Lines, at Pole 438763, Newton Rd, Omanaia
184 |  | INCD-32600-F-COBHAM ROAD | Kerikeri 181132 - Cobham Road |  | COBHAM ROAD | 2025-05-26 22:12 | 45803.9252 | 2025-05-27 01:00 | 45804.0417 | 1.4589 | 0.030274 | 572 | 52672.9167 | Unplanned | Defective Equipment | # Cable Fault, near Switch 685, Kerikeri Rd, Kerikeri
185 |  | INCD-32618-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-07-08 09:07 | 45846.3799 | 2025-07-08 11:53 | 45846.4951 | 0.06437 | 0.00038777 | 14 | 2324 | Planned | Planned Outage | # Upgrade Conductor Between Poles 416057 to 912783. Mangakahia Rd, Kaikohe
186 |  | INCD-32621-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-07-08 10:00 | 45846.417 | 2025-07-08 12:58 | 45846.5404 | 0.68434 | 0.00385 | 139 | 24707.25 | Planned | Planned Outage | # Re-sag Conductors Between Poles 408494 and 408497, Totara North Rd, Kaeo
187 |  | INCD-32630-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-05-28 16:17 | 45805.6787 | 2025-05-29 11:58 | 45806.4986 | 3.3422 | 0.011135 | 371 | 120667.1833 | Unplanned | Vegetation | # Tree through Lines, at Pole 429160, Duncan Rd, Awanui
188 |  | INCD-32636-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-05-28 16:19 | 45805.6796 | 2025-05-28 18:05 | 45805.7533 | 2.3313 | 0.04854 | 1752.4748 | 84170.8851 | Unplanned | Vegetation | # Vegetation Tripped 33kV Kaitaia to Taipa Line during Strong Winds, Duncan Rd, Kaitaia
189 |  | INCD-32636-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-05-28 16:19 | 45805.6796 | 2025-05-28 18:05 | 45805.7533 | 2.1421 | 0.044599 | 1610.1927 | 77337.114 | Unplanned | Vegetation | # Vegetation Tripped 33kV Kaitaia to Taipa Line during Strong Winds, Duncan Rd, Kaitaia
190 |  | INCD-32636-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-05-28 16:19 | 45805.6796 | 2025-05-28 18:05 | 45805.7533 | 2.2648 | 0.032582 | 1176.3325 | 81767.5676 | Unplanned | Vegetation | # Vegetation Tripped 33kV Kaitaia to Taipa Line during Strong Winds, Duncan Rd, Kaitaia
191 |  | INCD-32648-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-05-28 16:40 | 45805.6944 | 2025-05-28 22:03 | 45805.9187 | 0.38395 | 0.0012187 | 44 | 13862 | Unplanned | Unknown | # Recloser R_T01298 Tripped, West Coast Rd, Kaitaia
192 |  | INCD-32651-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-05-29 10:19 | 45806.4299 | 2025-05-29 12:04 | 45806.5028 | 0.098881 | 0.00094172 | 34 | 3570 | Unplanned | Vegetation | # Vegetation in Lines, at Switch 1636, Pamapuria
193 |  | INCD-32660-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-05-29 12:23 | 45806.516 | 2025-05-29 15:37 | 45806.6507 | 0.18807 | 0.00096942 | 35 | 6790 | Unplanned | Defective Equipment | # Defective Joint at Switch 023, Honeymoon Valley Rd, Taipa
194 |  | INCD-32675-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2025-05-29 16:18 | 45806.6791 | 2025-05-29 18:08 | 45806.7556 | 0.92047 | 0.019084 | 689 | 33232.5667 | Unplanned | Unknown | # Circuit Breaker CB0208 Tripped, Settlement Rd, Kawakawa
195 |  | INCD-32678-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-05-29 12:34 | 45806.5236 | 2025-05-29 19:14 | 45806.8014 | 0.2659 | 0.00066475 | 24 | 9600 | Unplanned | Defective Equipment | # Broken Crossarm, at Pole 413748, Te Ahu Rd, Te Kao
196 |  | INCD-32681-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-05-29 12:23 | 45806.516 | 2025-05-29 21:55 | 45806.9132 | 0.55451 | 0.00096942 | 35 | 20020 | Unplanned | Unknown | # Circuit Breaker CB1206 Tripped, at Switch 023, Honeymoon Valley Rd, Taipa
197 |  | INCD-32684-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-05-29 16:01 | 45806.6674 | 2025-05-30 13:54 | 45807.5792 | 0.30207 | 0.00038777 | 14 | 10906 | Unplanned | Defective Equipment | # SWER Line Down, at Pole 201968, Waiotehue Rd, Kaitaia
198 |  | INCD-32693-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-05-30 09:51 | 45807.4105 | 2025-05-31 12:43 | 45808.5299 | 1.3511 | 0.010054 | 186 | 48781.25 | Unplanned | Adverse Environment | # Broken Pole at Transformer T01024, West Coast Rd, Kaitaia
199 |  | INCD-32696-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-05-30 09:02 | 45807.3764 | 2025-05-30 13:43 | 45807.5715 | 0.31911 | 0.0011356 | 41 | 11521 | Unplanned | Defective Equipment | # Defective Joint at Pole 211773. Waiotemarama Gorge Rd, Omanaia
200 |  | INCD-32723-F-COBHAM ROAD | Kerikeri 181132 - Cobham Road |  | COBHAM ROAD | 2025-06-02 02:58 | 45810.1236 | 2025-06-02 03:20 | 45810.1389 | 0.0060935 | 0.00027698 | 10 | 220 | Unplanned | Third Party | # Repair Cable Fault near Switch 196, Kerikeri Rd, Kerikeri
201 |  | INCD-32729-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-06-02 21:27 | 45810.894 | 2025-06-02 22:52 | 45810.9528 | 1.6629 | 0.02033 | 734 | 60037.7667 | Unplanned | Wildlife | # BirdStrike on Line, Near Te Pua Road, Rangiahua
202 |  | INCD-32729-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-06-02 21:27 | 45810.894 | 2025-06-02 22:52 | 45810.9528 | 0.0023483 | 2.7698e-05 | 1 | 84.7833 | Unplanned | Wildlife | # BirdStrike on Line, Near Te Pua Road, Rangiahua
203 |  | INCD-32732-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-06-09 12:02 | 45817.5014 | 2025-06-09 13:04 | 45817.5444 | 0.012021 | 0.00019388 | 7 | 434 | Planned | Planned Outage | # Repair Damaged Conductor, near Pole 411469, Waiare Rd, Okaihau
204 |  | INCD-32735-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-06-03 10:01 | 45811.4175 | 2025-06-03 14:05 | 45811.5868 | 0.91149 | 0.0037392 | 135 | 32908.5 | Planned | Planned Outage | # Replace Pole 423408, SH1, Towai
205 |  | INCD-32738-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-06-25 09:46 | 45833.4069 | 2025-06-25 13:00 | 45833.5417 | 0.010747 | 5.5396e-05 | 2 | 388 | Planned | Planned Outage | # Vegetation Control beyond L074, West Coast Rd, Panguru
206 |  | INCD-32744-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-07-03 09:00 | 45841.3751 | 2025-07-03 12:16 | 45841.5109 | 4.7733 | 0.024457 | 882 | 172336.5 | Planned | Planned Outage | # Replace Pole 400897, Clear Vegetation, Kerikeri Inlet Rd, Kerikeri
207 |  | INCD-32747-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-07-04 09:02 | 45842.3767 | 2025-07-04 12:15 | 45842.5107 | 0.97605 | 0.0051241 | 185 | 35239.2 | Planned | Planned Outage | # New Switch on Pole 347724, Orakau Rd, Kaikohe
208 |  | INCD-32783-F-VICTORIA VALLEY | Kaitaia Transmission 151802 - Victoria Valley |  | VICTORIA VALLEY | 2025-06-04 14:08 | 45812.5891 | 2025-06-05 14:02 | 45813.5847 | 0.45346 | 0.034318 | 204.5057 | 16371.6333 | Unplanned | Vegetation | # Line Down near Pole 419405, Duncan Rd, Okahu Rd
209 |  | INCD-32783-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2025-06-04 14:08 | 45812.5891 | 2025-06-05 14:02 | 45813.5847 | 0.028254 | 0.0025205 | 15.0202 | 1020.0667 | Unplanned | Vegetation | # Line Down near Pole 419405, Duncan Rd, Okahu Rd
210 |  | INCD-32783-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-06-04 14:08 | 45812.5891 | 2025-06-05 14:02 | 45813.5847 | 0.080414 | 0.0071737 | 42.7498 | 2903.2667 | Unplanned | Vegetation | # Line Down near Pole 419405, Duncan Rd, Okahu Rd
211 |  | INCD-32783-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-06-04 14:08 | 45812.5891 | 2025-06-05 14:02 | 45813.5847 | 2.1714 | 0.019084 | 113.7243 | 78396.9667 | Unplanned | Vegetation | # Line Down near Pole 419405, Duncan Rd, Okahu Rd
212 |  | INCD-32792-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-06-04 15:23 | 45812.641 | 2025-06-04 16:59 | 45812.7076 | 0.013904 | 0.00016619 | 6 | 502 | Unplanned | Vegetation | # Remove Pine Tree from Line, at Pole 425918, Iwitaua Rd, Mangamuka
213 |  | INCD-32795-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-06-04 17:40 | 45812.7361 | 2025-06-04 20:32 | 45812.8556 | 0.43942 | 0.0026313 | 95 | 15865 | Unplanned | Adverse Weather | # Blown Fuse F2244, Onekura Rd, Pungaere
214 |  | INCD-32801-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-06-04 20:23 | 45812.8494 | 2025-06-04 22:49 | 45812.9507 | 1.4334 | 0.01047 | 378 | 51752.1667 | Unplanned | Adverse Weather | # Sectionaliser S1060 Tripped during Adverse Weather, Russell Rd, Paroa Bay
215 |  | INCD-32813-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-06-05 06:52 | 45813.2864 | 2025-06-05 11:01 | 45813.459 | 0.0012492 | 2.7698e-05 | 1 | 45.1 | Unplanned | Vegetation | # Tree through Line, at Pole 327241, Mangataipa Rd, Mangamuka Bridge
216 |  | INCD-32813-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-06-05 06:52 | 45813.2864 | 2025-06-05 11:01 | 45813.459 | 0.16964 | 0.0024928 | 90 | 6124.7 | Unplanned | Vegetation | # Tree through Line, at Pole 327241, Mangataipa Rd, Mangamuka Bridge
217 |  | INCD-32816-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-06-05 09:23 | 45813.3911 | 2025-06-05 14:29 | 45813.6035 | 0.22389 | 0.0024097 | 87 | 8083.45 | Unplanned | Vegetation | # Vegetation though Line at Pole 341639, Mangakahia Rd, Awarua
218 |  | INCD-32819-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-06-05 10:24 | 45813.4337 | 2025-06-05 12:25 | 45813.5174 | 1.1546 | 0.02562 | 925 | 41686.2333 | Unplanned | Unknown | # Circuit Breaker CB1406 Tripped, Whangatane Drive, Awanui
219 |  | INCD-32825-F-TI BAY | Haruru CB0606 - Ti Bay |  | TI BAY | 2025-05-28 22:17 | 45805.9285 | 2025-05-28 22:39 | 45805.9438 | 0.45986 | 0.020855 | 752.9605 | 16602.7796 | Unplanned | Defective Equipment | # Broken Tail at Pole 405229, Puketona Rd, Haruru
220 |  | INCD-32825-F-ONEWHERO | Haruru CB0608 - Onewhero |  | ONEWHERO | 2025-05-28 22:17 | 45805.9285 | 2025-05-28 22:39 | 45805.9438 | 0.0061315 | 0.00027807 | 10.0395 | 221.3704 | Unplanned | Defective Equipment | # Broken Tail at Pole 405229, Puketona Rd, Haruru
221 |  | INCD-32828-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-06-05 14:37 | 45813.6091 | 2025-06-05 15:41 | 45813.6535 | 0.46716 | 0.007423 | 268 | 16866.4833 | Unplanned | Defective Equipment | # Reattached Insulator, at Pole 404872, Manawaora Rd, Kawakawa
222 |  | INCD-32831-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-06-05 18:36 | 45813.775 | 2025-06-06 14:47 | 45814.616 | 0.059162 | 0.00016619 | 6 | 2136 | Unplanned | Defective Equipment | # Faulty Transformer T02041, Tipene Rd, Kawakawa
223 |  | INCD-32837-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-06-12 09:33 | 45820.3979 | 2025-06-12 13:58 | 45820.5819 | 0.10276 | 0.00038777 | 14 | 3710 | Planned | Planned Outage | # Replace Transformer Pole 411822, Pukepoto Rd, Kaikohe
224 |  | INCD-32843-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-06-06 03:15 | 45814.1351 | 2025-06-06 11:05 | 45814.4618 | 0.38372 | 0.016951 | 612 | 13854 | Unplanned | Vegetation | # Tree vs Lines, at L360, Turk Valley Rd, Pukenui
225 |  | INCD-32849-F-MATAURI BAY | Kaeo 191732 - Matauri Bay |  | MATAURI BAY | 2025-06-19 12:06 | 45827.5042 | 2025-06-19 15:28 | 45827.6444 | 0.01119 | 5.5396e-05 | 2 | 404 | Planned | Planned Outage | # Replace Crossarms on Pole 435077, Matauri Bay Rd, Kaeo
226 |  | INCD-32852-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-06-06 11:36 | 45814.4833 | 2025-06-06 13:11 | 45814.5493 | 0.055257 | 0.00058165 | 21 | 1995 | Unplanned | Adverse Environment | # Replaced Leaning Pole 406012, Taita Rd, Omanaia
227 |  | INCD-32855-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-06-06 14:09 | 45814.5896 | 2025-06-06 15:26 | 45814.6431 | 0.031991 | 0.00041547 | 15 | 1155 | Unplanned | Vegetation | # Tree through Line, at Pole 419390, Paranui Rd, Taipa
228 |  | INCD-32858-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-06-06 13:26 | 45814.5597 | 2025-06-06 16:58 | 45814.7069 | 0.052847 | 0.00024928 | 9 | 1908 | Unplanned | Defective Equipment | # Broken Jumper at Pole 419671, Cook Rd, Utakura
229 |  | INCD-32861-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-06-06 15:47 | 45814.6576 | 2025-06-06 19:05 | 45814.7949 | 7.0033 | 0.04451 | 1607 | 252845.4667 | Unplanned | Vegetation | # Trees vs Line, By Pole 415135, SH10, Taipa
230 |  | INCD-32867-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-06-06 13:58 | 45814.5819 | 2025-06-06 21:36 | 45814.9 | 0.10148 | 0.00022158 | 8 | 3664 | Unplanned | Defective Equipment | # Broken Jumper at Switch 1203, Big Flat Rd, Pukenui
231 |  | INCD-32873-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-06-07 08:07 | 45815.3385 | 2025-06-07 12:44 | 45815.5306 | 0.80142 | 0.014043 | 507 | 28934.55 | Unplanned | Vegetation | # Trees on Lines, near Link L875, Kunicich Rd, Kaitaia
232 |  | INCD-32879-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-06-07 13:14 | 45815.5512 | 2025-06-07 18:34 | 45815.7734 | 2.4462 | 0.013461 | 486 | 88316.3333 | Unplanned | Vegetation | # Tree vs Lines, at Pole 436764, SH10, Kaeo
233 |  | INCD-32888-F-PUKETONA | Haruru CB0607 - Puketona |  | PUKETONA | 2025-06-13 11:05 | 45821.4618 | 2025-06-13 14:07 | 45821.5882 | 0.073842 | 0.00063705 | 18 | 2666 | Planned | Planned Outage | # Replace Switch 122, Puketona Rd, Haruru Falls
234 |  | INCD-32897-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-07-08 09:32 | 45846.3973 | 2025-07-08 12:55 | 45846.5379 | 1.3058 | 0.0064536 | 233 | 47143.6667 | Planned | Planned Outage | # Replace Poles, New Switch 1839, Taupo Bay Rd, Taipa
235 |  | INCD-32903-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-07-09 09:23 | 45847.3912 | 2025-07-09 14:10 | 45847.5905 | 0.17462 | 0.00060935 | 22 | 6304.4667 | Planned | Planned Outage | # Replace Poles, Cross-arms, SH10, Kaeo
236 |  | INCD-32903-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-07-09 09:23 | 45847.3912 | 2025-07-09 14:10 | 45847.5905 | 0.15827 | 0.00055396 | 20 | 5714.3333 | Planned | Planned Outage | # Replace Poles, Cross-arms, SH10, Kaeo
237 |  | INCD-32909-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2025-06-18 10:31 | 45826.4382 | 2025-06-18 15:47 | 45826.6576 | 0.13029 | 0.00044316 | 16 | 4704 | Planned | Planned Outage | # Raised Low Lines, Replace Pole 440136, SH10, Kaeo
238 |  | INCD-32924-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-06-10 14:48 | 45818.617 | 2025-06-10 14:51 | 45818.619 | 0.095437 | 0.033487 | 1209 | 3445.65 | Unplanned | Human Error | # Recloser R1785 Tripped, Inland Rd, Lake Ohia
239 |  | INCD-32927-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-06-10 18:54 | 45818.7875 | 2025-06-11 14:18 | 45819.5958 | 3.5328 | 0.0048194 | 174 | 127549 | Unplanned | Vegetation | # Tree Damaged Conductor and Multiple Assets, Beyond Link L925, Pukenui
240 |  | INCD-32930-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-06-10 19:27 | 45818.8108 | 2025-06-10 22:09 | 45818.9229 | 0.35304 | 0.013544 | 489 | 12746.25 | Unplanned | Vegetation | # Tree in Line, at Pole 419852, Okaka Rd, Kaikohe
241 |  | INCD-32936-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-06-11 09:01 | 45819.3759 | 2025-06-11 14:49 | 45819.617 | 1.3467 | 0.0038777 | 140 | 48619.6667 | Planned | Planned Outage | # Change Poles Beyond S1009, Takou Bay, Waipapa
242 |  | INCD-32942-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2025-06-11 09:48 | 45819.4084 | 2025-06-11 09:57 | 45819.4149 | 0.16833 | 0.018197 | 657 | 6077.25 | Unplanned | Human Error | # Circuit Breaker CB173332 Operated instead of CB173352, Mt Pokaka Substation
243 |  | INCD-32942-F-TIMBER MILL | Mt Pokaka 171132 - Timber Mill |  | TIMBER MILL | 2025-06-11 09:48 | 45819.4084 | 2025-06-11 09:57 | 45819.4149 | 1.8465e-06 | 0.00011079 | 4 | 0.066667 | Unplanned | Human Error | # Circuit Breaker CB173332 Operated instead of CB173352, Mt Pokaka Substation
244 |  | INCD-32942-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-06-11 09:48 | 45819.4084 | 2025-06-11 09:57 | 45819.4149 | 0.045964 | 0.0054288 | 196 | 1659.4667 | Unplanned | Human Error | # Circuit Breaker CB173332 Operated instead of CB173352, Mt Pokaka Substation
245 |  | INCD-32945-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2025-06-18 09:37 | 45826.4007 | 2025-06-18 10:50 | 45826.4514 | 0.22039 | 0.0030191 | 109 | 7957 | Planned | Planned Outage | # Maintenance on Cable Termination, at Pole 427525, Donald Lane, Kaitaia
246 |  | INCD-32951-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2025-06-26 10:11 | 45834.4243 | 2025-06-26 13:40 | 45834.5694 | 0.011578 | 5.5396e-05 | 2 | 418 | Planned | Planned Outage | # Replace Pole 402149, Wiroa Rd, Kerikeri
247 |  | INCD-32954-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-06-11 16:42 | 45819.6958 | 2025-06-11 19:41 | 45819.8201 | 0.059495 | 0.00033237 | 12 | 2148 | Unplanned | Adverse Environment | # Relocate Pole 430283, Due to Slip, Paua Rd, Pukenui
248 |  | INCD-32960-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-07-09 10:23 | 45847.4326 | 2025-07-09 13:00 | 45847.5417 | 0.017394 | 0.00011079 | 4 | 628 | Planned | Planned Outage | # Replace Tails, LV Fuses on Transformer T00604, West Coast Rd, Kaikohe
249 |  | INCD-32969-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-07-10 09:07 | 45848.3799 | 2025-07-10 14:58 | 45848.6236 | 1.3577 | 0.0038777 | 140 | 49018 | Planned | Planned Outage | # Verify Ring Main Unit Wiring RMU197, Tokerau Beach, Taipa
250 |  | INCD-32975-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-07-02 09:05 | 45840.3785 | 2025-07-02 14:45 | 45840.6146 | 0.037669 | 0.00011079 | 4 | 1360 | Planned | Planned Outage | # Vegetation Control beyond Pole 434514, Wharekawa Rd, Omanaia
251 |  | INCD-32984-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-06-14 00:22 | 45822.0155 | 2025-06-14 04:34 | 45822.1904 | 0.50235 | 0.0019942 | 72 | 18136.8 | Unplanned | Defective Equipment | # Insulator Pulled Out of Crossarm, Pole 415226, West Coast Rd, Kaikohe
252 |  | INCD-32987-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-06-14 16:36 | 45822.6917 | 2025-06-14 19:11 | 45822.7993 | 0.085863 | 0.00055396 | 20 | 3100 | Unplanned | Unknown | # Blown Fuse F2405, Mahinepua Rd, Kaeo
253 |  | INCD-33002-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-07-09 09:54 | 45847.4124 | 2025-07-09 15:16 | 45847.6363 | 2.679 | 0.0087525 | 304 | 96723.5 | Planned | Planned Outage | # Replace Pole 414515, Install Transformer T20080, Runaruna Rd, Kaitaia
254 |  | INCD-33014-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-07-16 09:35 | 45854.3993 | 2025-07-16 14:29 | 45854.6035 | 0.11323 | 0.00041547 | 15 | 4088 | Planned | Planned Outage | # Replace Poles,Transformer T00997, Broadwood Rd, Kaitaia
255 |  | INCD-33017-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-06-17 09:32 | 45825.3971 | 2025-06-17 09:35 | 45825.3996 | 0.01648 | 0.0047086 | 170 | 595 | Planned | Planned Outage | # Replacing Poles from Pole 427491 to 430381, Kaitaia-Awaroa Rd, Herekino
256 |  | INCD-33020-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2025-06-17 09:37 | 45825.4007 | 2025-06-17 13:07 | 45825.5465 | 0.94709 | 0.019139 | 691 | 34193.8 | Unplanned | Defective Equipment | # Suspension Insulator Broken, at Pole 402839, SH11, Kawakawa
257 |  | INCD-33023-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-06-17 09:45 | 45825.4062 | 2025-06-17 15:58 | 45825.6653 | 1.9341 | 0.0053457 | 193 | 69830.1667 | Planned | Planned Outage | # Replacing Poles 427491 to 430381, Kaitaia Awaroa Rd, Herekino
258 |  | INCD-33026-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-07-10 09:34 | 45848.3986 | 2025-07-10 14:42 | 45848.6125 | 0.52039 | 0.0016896 | 61 | 18788 | Planned | Planned Outage | # Upgrade Conductor, Install Sectionaliser S1068, Sandhills Rd, Ahipara
259 |  | INCD-33029-F-RIVERVIEW | Waipapa 041682 - Riverview |  | RIVERVIEW | 2025-07-14 09:07 | 45852.3799 | 2025-07-14 12:24 | 45852.5167 | 0.4256 | 0.0021604 | 78 | 15366 | Planned | Planned Outage | # Vegetation Control, Beyond Sectional S157, Skudders Beach Rd, Kerikeri
260 |  | INCD-33035-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-07-28 09:05 | 45866.3785 | 2025-07-28 12:56 | 45866.5389 | 0.051185 | 0.00022158 | 8 | 1848 | Planned | Planned Outage | # Vegetation Control, Poles 437252 to 437256, Te Kahikatoa Rd, Kaeo
261 |  | INCD-33038-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-07-30 09:39 | 45868.4021 | 2025-07-30 14:16 | 45868.5944 | 0.19948 | 0.00072014 | 26 | 7202 | Planned | Planned Outage | # Vegetation Control, Pole 425539, Tapuhi Rd, Kawakawa
262 |  | INCD-33041-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-08-04 09:07 | 45873.3799 | 2025-08-04 10:51 | 45873.4521 | 0.046089 | 0.00044316 | 16 | 1664 | Planned | Planned Outage | # Vegetation Control, Beyond Link L589, Tapuhi Rd, Kawakawa
263 |  | INCD-33044-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-08-06 09:00 | 45875.3753 | 2025-08-06 11:23 | 45875.474 | 0.3621 | 0.0025482 | 92 | 13073.2 | Planned | Planned Outage | # Vegetation Control, Beyond Recloser R050, Callaghan Rd, Kawakawa
264 |  | INCD-33053-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-07-21 09:09 | 45859.3812 | 2025-07-21 13:16 | 45859.5528 | 0.22576 | 0.00091403 | 33 | 8151 | Planned | Planned Outage | # Vegetation Control at Poles 408533, 408537, 408538, Pupuke Mangapa Rd, Kaeo
265 |  | INCD-33056-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-07-23 09:05 | 45861.3785 | 2025-07-23 13:13 | 45861.5507 | 0.082429 | 0.00033237 | 12 | 2976 | Planned | Planned Outage | # Vegetation Control, Poles 408586 to 45533, Pupuke Mangapa Rd, Kaeo
266 |  | INCD-33062-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-06-20 10:56 | 45828.4553 | 2025-06-20 12:33 | 45828.5229 | 0.23716 | 0.0024374 | 88 | 8562.4 | Unplanned | Defective Equipment | # Repaired Link L185, at R587, Te Pua Rd, Kaikohe
267 |  | INCD-33071-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-07-02 10:09 | 45840.4229 | 2025-07-02 13:11 | 45840.5493 | 0.0539 | 0.00044316 | 16 | 1946 | Planned | Planned Outage | # Replace Transformer T00856, SH1, Okaihau
268 |  | INCD-33074-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-07-17 09:34 | 45855.3986 | 2025-07-17 12:57 | 45855.5396 | 0.08434 | 0.00041547 | 15 | 3045 | Planned | Planned Outage | # Vegetation Control, Near Pole 434829, SH12, Omanaia
269 |  | INCD-33077-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-07-17 22:30 | 45855.9375 | 2025-07-18 03:40 | 45856.1528 | 1.7384 | 0.0093895 | 339 | 62762 | Planned | Planned Outage | # Replace Transformer T02788, Fairlie Crescent, Opononi
270 |  | INCD-33083-F-OXFORD STREET | Okahu CB1108 - Oxford Street |  | OXFORD STREET | 2025-06-23 17:00 | 45831.7085 | 2025-06-23 18:18 | 45831.7625 | 0.39086 | 0.014968 | 466.2555 | 14111.6264 | Unplanned | Defective Equipment | # Broken Lead on Switch 700, SH1, Kaitaia
271 |  | INCD-33083-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-06-23 17:00 | 45831.7085 | 2025-06-23 18:18 | 45831.7625 | 0.090077 | 0.0041854 | 130.3789 | 3252.1224 | Unplanned | Defective Equipment | # Broken Lead on Switch 700, SH1, Kaitaia
272 |  | INCD-33083-F-VICTORIA VALLEY | Kaitaia Transmission 151802 - Victoria Valley |  | VICTORIA VALLEY | 2025-06-23 17:00 | 45831.7085 | 2025-06-23 18:18 | 45831.7625 | 0.10976 | 0.0051001 | 158.8722 | 3962.8511 | Unplanned | Defective Equipment | # Broken Lead on Switch 700, SH1, Kaitaia
273 |  | INCD-33083-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-06-23 17:00 | 45831.7085 | 2025-06-23 18:18 | 45831.7625 | 0.11406 | 0.013138 | 409.2687 | 4118.016 | Unplanned | Defective Equipment | # Broken Lead on Switch 700, SH1, Kaitaia
274 |  | INCD-33083-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2025-06-23 17:00 | 45831.7085 | 2025-06-23 18:18 | 45831.7625 | 0.0077549 | 0.00036034 | 11.2247 | 279.984 | Unplanned | Defective Equipment | # Broken Lead on Switch 700, SH1, Kaitaia
275 |  | INCD-33086-F-SOUTH ROAD | Okahu CB1105 - South Road |  | SOUTH ROAD | 2025-06-24 10:28 | 45832.4359 | 2025-06-24 12:22 | 45832.5153 | 0.19493 | 0.0017727 | 64 | 7037.8667 | Unplanned | Defective Equipment | # Broken Lead at Switch 700, SH1, Kaitaia
276 |  | INCD-33086-F-OXFORD STREET | Okahu CB1108 - Oxford Street |  | OXFORD STREET | 2025-06-24 10:28 | 45832.4359 | 2025-06-24 12:22 | 45832.5153 | 0.56957 | 0.0051795 | 187 | 20563.7667 | Unplanned | Defective Equipment | # Broken Lead at Switch 700, SH1, Kaitaia
277 |  | INCD-33092-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-06-25 10:36 | 45833.4417 | 2025-06-25 12:32 | 45833.5222 | 1.7646 | 0.019555 | 706 | 63709.45 | Unplanned | Third Party | # Third Party tripped Recloser R587, Te Pua Rd, Kaikohe
278 |  | INCD-33092-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-06-25 10:36 | 45833.4417 | 2025-06-25 12:32 | 45833.5222 | 0.003212 | 2.7698e-05 | 1 | 115.9667 | Unplanned | Third Party | # Third Party tripped Recloser R587, Te Pua Rd, Kaikohe
279 |  | INCD-33095-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-06-25 10:30 | 45833.4375 | 2025-06-25 14:38 | 45833.6097 | 1.0853 | 0.0043762 | 158 | 39184 | Planned | Planned Outage | # Replace Crossarms on Pole 404872, Kempthorne Rd, Russell
280 |  | INCD-33098-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-07-15 09:35 | 45853.3993 | 2025-07-15 13:50 | 45853.5764 | 0.43084 | 0.0016896 | 61 | 15555 | Planned | Planned Outage | # Network Additions and Alterations beyond Switch 229, Sandhills Rd, Kaitaia
281 |  | INCD-33101-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-07-31 09:10 | 45869.3819 | 2025-07-31 13:29 | 45869.5618 | 0.31564 | 0.0012187 | 44 | 11396 | Planned | Planned Outage | # Replace Poles between 437892 and 437916, Taukou Bay Rd, Waipapa
282 |  | INCD-33104-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-06-25 11:00 | 45833.4583 | 2025-06-25 14:53 | 45833.6201 | 0.28396 | 0.0012187 | 44 | 10252 | Unplanned | Unknown | # Recloser Found Open, R_T01298, West Coast Rd, Okahu Rd
283 |  | INCD-33107-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-07-22 09:00 | 45860.375 | 2025-07-22 15:23 | 45860.641 | 0.45086 | 0.0012187 | 44 | 16278 | Planned | Planned Outage | # Pole Replacements beyond Link L525, Takou Bay Rd, Waipapa
284 |  | INCD-33146-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-06-26 19:31 | 45834.8129 | 2025-06-26 22:51 | 45834.9521 | 0.58629 | 0.0068413 | 196 | 21167.5 | Unplanned | Wildlife | # Remove Possum from Pole 409167, Puketotara Rd, Waipapa
285 |  | INCD-33152-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-06-26 23:01 | 45834.9592 | 2025-06-27 03:37 | 45835.1507 | 0.44013 | 0.0041824 | 151 | 15890.2833 | Unplanned | Vegetation | # Vegetation on Line, Beyond Link L304, Pekerau Rd, Lake Ohia
286 |  | INCD-33155-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-06-27 03:02 | 45835.1267 | 2025-06-27 05:28 | 45835.2278 | 1.6638 | 0.016591 | 599 | 60071.5167 | Unplanned | Vegetation | # Vegetation Contact with Line, Near Pole 041692, Waipapa
287 |  | INCD-33164-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-06-27 04:56 | 45835.2059 | 2025-06-27 10:17 | 45835.4285 | 0.19081 | 0.0016896 | 49.5704 | 6888.9333 | Unplanned | Adverse Weather | # Line down beyond Pole 415898, Masters Access Rd, Ahipara
288 |  | INCD-33164-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-06-27 04:56 | 45835.2059 | 2025-06-27 10:17 | 45835.4285 | 3.4091 | 0.038223 | 1121.4296 | 123082.25 | Unplanned | Adverse Weather | # Line down beyond Pole 415898, Masters Access Rd, Ahipara
289 |  | INCD-33182-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-06-27 04:21 | 45835.1813 | 2025-06-27 11:55 | 45835.4965 | 0.22502 | 0.00066475 | 24 | 8124 | Unplanned | Defective Equipment | # Broken Stay Contacting Transformer Bushing T01120, Te Ahu Rd, Te Kao
290 |  | INCD-33215-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-06-30 12:57 | 45838.5396 | 2025-06-30 21:51 | 45838.9104 | 0.30556 | 0.00099712 | 36 | 11032 | Unplanned | Defective Equipment | # Fix Earthing at T08635 Transformer, Edmonds Rd, Kerikeri Inlet
291 |  | INCD-33227-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-06-30 13:53 | 45838.5783 | 2025-06-30 14:55 | 45838.6215 | 0.25739 | 0.025593 | 924 | 9292.8 | Unplanned | Adverse Environment | # Broken Binders at Pole 410769, Quarry Rd, Awanui
292 |  | INCD-33230-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-07-22 10:01 | 45860.4174 | 2025-07-22 12:38 | 45860.5264 | 0.0086971 | 5.5396e-05 | 2 | 314 | Planned | Planned Outage | # Upgrade Transformer T20089, SH10, Kapiro
293 |  | INCD-33233-F-HONE HEKE ROAD | Kerikeri 181182 - Hone Heke Road |  | HONE HEKE ROAD | 2025-07-01 00:32 | 45839.0222 | 2025-07-01 04:25 | 45839.184 | 0.38076 | 0.0016342 | 59 | 13747 | Unplanned | Unknown | # Fuse L002 Blown, Hone Heke Rd, Kerikeri
294 |  | INCD-33242-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-07-01 18:10 | 45839.7568 | 2025-07-01 18:38 | 45839.7764 | 0.52527 | 0.025593 | 924 | 18964.3667 | Unplanned | Defective Equipment | # Joint Failure at Switch 118, Gill Rd, Awanui
295 |  | INCD-33245-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-07-09 10:02 | 45847.4181 | 2025-07-09 12:21 | 45847.5146 | 0.0616 | 0.00044316 | 16 | 2224 | Planned | Planned Outage | # Relocate Pole 322411, Omanaia Rd, Omanaia
296 |  | INCD-33251-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-07-15 10:02 | 45853.4181 | 2025-07-15 15:06 | 45853.6294 | 0.63214 | 0.0071737 | 259 | 22822.8 | Planned | Planned Outage | # Replace Crossarms, Pole, at Poles 438775, 438818, SH12, Omanaia
297 |  | INCD-33254-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-07-03 06:30 | 45841.2708 | 2025-07-03 10:33 | 45841.4396 | 0.22776 | 0.0010802 | 39 | 8223 | Unplanned | Adverse Weather | # SWER Recloser R_T03344 Tripped, due to DDO at T01702, Paranui Rd, Taipa
298 |  | INCD-33257-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-07-03 09:23 | 45841.391 | 2025-07-03 12:46 | 45841.5319 | 0.19679 | 0.00096942 | 35 | 7105 | Unplanned | Adverse Weather | # Fuse F2255 Blew, Honeymoon Valley, Taipa
299 |  | INCD-33260-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-07-03 11:47 | 45841.4911 | 2025-07-03 11:58 | 45841.4988 | 0.41465 | 0.04976 | 1796.5257 | 14970.4547 | Unplanned | Third Party | # Third Party Interference at Taipa Substation Requiring 33kV Outage
300 |  | INCD-33260-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-07-03 11:47 | 45841.4911 | 2025-07-03 11:58 | 45841.4988 | 0.35627 | 0.032637 | 1178.3124 | 12862.7349 | Unplanned | Third Party | # Third Party Interference at Taipa Substation Requiring 33kV Outage
301 |  | INCD-33260-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-07-03 11:47 | 45841.4911 | 2025-07-03 11:58 | 45841.4988 | 0.38376 | 0.044626 | 1611.1619 | 13855.4438 | Unplanned | Third Party | # Third Party Interference at Taipa Substation Requiring 33kV Outage
302 |  | INCD-33266-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-07-03 13:59 | 45841.5824 | 2025-07-03 15:54 | 45841.6625 | 0.21468 | 0.0041824 | 151 | 7750.95 | Unplanned | Adverse Weather | # Sectionaliser S1004 Tripped during Adverse Weather, Fairburn Rd, Kaitaia
303 |  | INCD-33284-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-07-03 15:40 | 45841.6528 | 2025-07-03 18:17 | 45841.7618 | 0.1522 | 0.00096942 | 35 | 5495 | Unplanned | Adverse Weather | # F2255 Operated during Adverse Weather, Honeymoon Valley, Taipa
304 |  | INCD-33290-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-07-03 18:11 | 45841.7576 | 2025-07-04 22:56 | 45842.9556 | 0.72723 | 0.0059827 | 51 | 26256 | Unplanned | Defective Equipment | # Defective Insulator at Pole 408586, Pupuke Mangapa Rd, Kaeo
305 |  | INCD-33308-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-07-10 00:01 | 45848.0005 | 2025-07-10 02:53 | 45848.1199 | 2.5174 | 0.014763 | 533 | 90887.6333 | Planned | Planned Outage | # Damaged Conductor, Binders, at Pole 416035, Mangakahia Rd, Kaikohe
306 |  | INCD-33311-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-07-15 09:00 | 45853.375 | 2025-07-15 14:00 | 45853.5833 | 1.2547 | 0.0041824 | 151 | 45300 | Planned | Planned Outage | # Tree Clearing, Poles 418875 to 418873, Fairburn Rd, Kaitaia
307 |  | INCD-33326-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-07-06 07:39 | 45844.3184 | 2025-07-06 11:40 | 45844.4861 | 0.011734 | 0.0010248 | 37 | 423.65 | Unplanned | Vegetation | # Conductor Down near Pole 418774, Taumata Rd, Okahu Rd
308 |  | INCD-33326-F-VICTORIA VALLEY | Kaitaia Transmission 151802 - Victoria Valley |  | VICTORIA VALLEY | 2025-07-06 07:39 | 45844.3184 | 2025-07-06 11:40 | 45844.4861 | 0.058354 | 0.0050964 | 184 | 2106.8 | Unplanned | Vegetation | # Conductor Down near Pole 418774, Taumata Rd, Okahu Rd
309 |  | INCD-33326-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-07-06 07:39 | 45844.3184 | 2025-07-06 11:40 | 45844.4861 | 0.1307 | 0.0041824 | 151 | 4718.7333 | Unplanned | Vegetation | # Conductor Down near Pole 418774, Taumata Rd, Okahu Rd
310 |  | INCD-33326-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2025-07-06 07:39 | 45844.3184 | 2025-07-06 11:40 | 45844.4861 | 0.0041228 | 0.00036007 | 13 | 148.85 | Unplanned | Vegetation | # Conductor Down near Pole 418774, Taumata Rd, Okahu Rd
311 |  | INCD-33329-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-07-14 10:03 | 45852.4187 | 2025-07-14 13:20 | 45852.5556 | 0.56099 | 0.0028529 | 103 | 20254 | Planned | Planned Outage | # Replace Switch 118 with Omniruptor, Gill Rd, Awanui
312 |  | INCD-33353-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-07-10 01:05 | 45848.0451 | 2025-07-10 02:13 | 45848.0924 | 0.76832 | 0.019333 | 589 | 27739.35 | Unplanned | Unknown | # Circuit Breaker Tripped 041692, Puketi Feeder, Waipapa
313 |  | INCD-33356-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-07-10 10:06 | 45848.4206 | 2025-07-10 14:21 | 45848.5979 | 2.5822 | 0.029581 | 606 | 93228.9667 | Unplanned | Vegetation | # Bamboo Damaged Conductor, Beyond Switch 669, Waipapa West Rd, Waipapa
314 |  | INCD-33362-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-07-10 12:20 | 45848.5139 | 2025-07-10 14:18 | 45848.5958 | 0.2582 | 0.0021881 | 79 | 9322 | Unplanned | Defective Equipment | # Broken Insulator at Link L139, Virtue Crescent, Karikari Peninsula
315 |  | INCD-33365-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-07-10 12:52 | 45848.5359 | 2025-07-10 18:31 | 45848.7715 | 1.9151 | 0.013073 | 472 | 69143.5333 | Unplanned | Third Party | # Truck vs Conductor, near Pole 436834, Whangaroa Rd, Kaeo
316 |  | INCD-33368-F-KAIKOHE | Kaikohe CB0107 - Kaikohe |  | KAIKOHE | 2025-07-14 03:04 | 45852.1278 | 2025-07-14 03:55 | 45852.1632 | 0.13096 | 0.002659 | 96 | 4728 | Planned | Planned Outage | # Isolation for Close Approach Consent, at Link 119, Park Rd, Kaikohe
317 |  | INCD-33371-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-07-10 16:32 | 45848.6889 | 2025-07-10 17:43 | 45848.7382 | 0.14552 | 0.0020496 | 74 | 5254 | Unplanned | Third Party | # Isolation of Overhead Lines due to Truck Accident, Pole 430736, Day 1, Whangape Rd, Herekino
318 |  | INCD-33383-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-07-11 10:03 | 45849.4187 | 2025-07-11 13:30 | 45849.5625 | 0.42427 | 0.0020496 | 74 | 15318 | Unplanned | Third Party | # Isolation of Overhead Lines due to Truck Accident, Pole 430736, Day 2, Whangape Rd, Herekino
319 |  | INCD-33389-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-07-11 11:35 | 45849.4824 | 2025-07-11 18:42 | 45849.7789 | 2.1525 | 0.013461 | 486 | 77714.2333 | Unplanned | Vegetation | # Trees vs Line, Tripped Circuit Breaker, Whangaroa Rugby Club, Kaeo
320 |  | INCD-33395-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-07-11 11:16 | 45849.4694 | 2025-07-11 13:47 | 45849.5743 | 0.28858 | 0.0019111 | 69 | 10419 | Unplanned | Vegetation | # Branch on Line, Fuse F2017, Whalers Rd, Pukenui
321 |  | INCD-33401-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-07-11 12:37 | 45849.5257 | 2025-07-12 10:24 | 45850.4333 | 1.267 | 0.00096942 | 35 | 45745 | Unplanned | Vegetation | # Tree vs Line, Pole 419371, Honeymoon Valley Rd, Taipa
322 |  | INCD-33407-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-07-11 13:26 | 45849.5597 | 2025-07-11 15:52 | 45849.6611 | 0.80365 | 0.0084201 | 304 | 29015 | Unplanned | Vegetation | # Tree Contacts on Conductor, Beyond Recloser R1850, Kaikohe
323 |  | INCD-33413-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-07-11 15:24 | 45849.6416 | 2025-07-11 17:15 | 45849.7187 | 1.415 | 0.022851 | 825 | 51087.2167 | Unplanned | Adverse Weather | # Repair Tail on L157, Hospital Rd, Mangonui
324 |  | INCD-33416-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-07-11 17:15 | 45849.7188 | 2025-07-11 19:33 | 45849.8146 | 0.12935 | 0.0012464 | 45 | 4670 | Unplanned | Vegetation | # Tree Fire Affecting Conductor, at Pole 412376, Te Tio Rd, Kaikohe
325 |  | INCD-33422-F-KARETU | Kawakawa CB0210 - Karetu |  | KARETU | 2025-07-24 10:00 | 45862.4167 | 2025-07-24 16:30 | 45862.6875 | 0.31487 | 0.0013849 | 50 | 11368 | Planned | Planned Outage | # Re-Sag Conductor, Replace Hardware, near Switch 1357, Waikare Rd, Kawakawa
326 |  | INCD-33425-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-08-05 09:40 | 45874.4028 | 2025-08-05 14:53 | 45874.6201 | 0.46626 | 0.0015788 | 57 | 16834 | Planned | Planned Outage | # Planned Maintenance, Beyond Switch 340, Mangatoetoe Rd, Kaikohe
327 |  | INCD-33428-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-08-05 10:14 | 45874.4264 | 2025-08-05 13:36 | 45874.5667 | 0.41657 | 0.0023543 | 85 | 15040 | Planned | Planned Outage | # Upgrade Transformers T03567, T03239, Earthbank T09124, Beyond L729, Kawakawa
328 |  | INCD-33440-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-07-13 10:20 | 45851.4306 | 2025-07-13 11:05 | 45851.4618 | 0.052349 | 0.0011633 | 42 | 1890 | Unplanned | Vegetation | # Tree in Overhead Lines, Pole 417775, RedCliffs Rd, Waipapa
329 |  | INCD-33443-F-POKAPU | Moerewa 031312 - Pokapu |  | POKAPU | 2025-07-13 19:05 | 45851.7949 | 2025-07-14 14:05 | 45852.5868 | 0.38076 | 0.0040716 | 147 | 13746.9333 | Unplanned | Adverse Weather | # Pole 425480 Collapsed due to Adverse Weather, Daveys Rd, Moerewa
330 |  | INCD-33455-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-08-01 09:40 | 45870.4028 | 2025-08-01 13:52 | 45870.5778 | 0.1047 | 0.00041547 | 15 | 3780 | Planned | Planned Outage | # 5820 : T00234 : Hauparua Ln new Tx T20090 : Network Maintenance
331 |  | INCD-33458-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2025-07-15 06:38 | 45853.2767 | 2025-07-15 07:40 | 45853.3194 | 0.60675 | 0.018641 | 673 | 21906.15 | Unplanned | Defective Equipment | # 33kV Circuit Breaker Tripped, Mt Pokaka Substation
332 |  | INCD-33458-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-07-15 06:38 | 45853.2767 | 2025-07-15 07:40 | 45853.3194 | 0.048045 | 0.0055119 | 199 | 1734.6167 | Unplanned | Defective Equipment | # 33kV Circuit Breaker Tripped, Mt Pokaka Substation
333 |  | INCD-33458-F-TIMBER MILL | Mt Pokaka 171132 - Timber Mill |  | TIMBER MILL | 2025-07-15 06:38 | 45853.2767 | 2025-07-15 07:40 | 45853.3194 | 0.0068192 | 0.00011079 | 4 | 246.2 | Unplanned | Defective Equipment | # 33kV Circuit Breaker Tripped, Mt Pokaka Substation
334 |  | INCD-33464-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-07-15 07:01 | 45853.2924 | 2025-07-15 08:37 | 45853.359 | 0.023931 | 0.00024928 | 9 | 864 | Unplanned | Lightning | # Lightning Strike Blew Fuse F2075, Waimamaku Beach Rd, Omanaia
335 |  | INCD-33479-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-07-15 15:19 | 45853.6382 | 2025-07-16 12:56 | 45854.5389 | 0.12724 | 0.0014957 | 54 | 4594 | Unplanned | Defective Equipment | # Broken Crossarm, at Pole 405642, SH12, Omanaia
336 |  | INCD-33482-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-07-15 14:11 | 45853.591 | 2025-07-15 16:21 | 45853.6813 | 0.025205 | 0.00019388 | 7 | 910 | Unplanned | Lightning | # Lightning Strike Blew Fuse L153, Kohukohu Rd, Te Karae
337 |  | INCD-33485-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-07-15 19:11 | 45853.7993 | 2025-07-15 21:20 | 45853.8889 | 0.12669 | 0.00099712 | 36 | 4574 | Unplanned | Adverse Weather | # Repair Termination at Pole 410871, Sandhills Rd, Kaitaia
338 |  | INCD-33494-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-07-16 09:37 | 45854.4007 | 2025-07-16 14:11 | 45854.591 | 0.075892 | 0.00027698 | 10 | 2740 | Unplanned | Vegetation | # Vegetation took Line Down, Pole 426609, Pipiwai Rd, Kaikohe
339 |  | INCD-33500-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-07-22 09:31 | 45860.3965 | 2025-07-22 14:09 | 45860.5896 | 2.2715 | 0.0081708 | 295 | 82010 | Planned | Planned Outage | # Install Sectionaliser S1099, Foreshore Rd, Ahipapa
340 |  | INCD-33509-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-07-25 09:46 | 45863.4069 | 2025-07-25 13:37 | 45863.5674 | 0.46067 | 0.0019942 | 72 | 16632 | Planned | Planned Outage | # Replace Pole 430058, Fuses and Transformer T01703, Waharua Rd, Te Hapua
341 |  | INCD-33521-F-RANUI AVENUE | Kerikeri 181172 - Ranui Ave |  | RANUI AVENUE | 2025-07-17 09:02 | 45855.3765 | 2025-07-17 09:09 | 45855.3811 | 0.10321 | 0.015677 | 565.9982 | 3726.155 | Unplanned | Human Error | # Line Tripped during Planned Job, Feeder 181172, Mill Lane, Kerikeri
342 |  | INCD-33521-F-COBHAM ROAD | Kerikeri 181132 - Cobham Road |  | COBHAM ROAD | 2025-07-17 09:02 | 45855.3765 | 2025-07-17 09:09 | 45855.3811 | 0.00018267 | 2.7747e-05 | 1.0018 | 6.595 | Unplanned | Human Error | # Line Tripped during Planned Job, Feeder 181172, Mill Lane, Kerikeri
343 |  | INCD-33524-F-HONE HEKE ROAD | Kerikeri 181182 - Hone Heke Road |  | HONE HEKE ROAD | 2025-07-17 09:02 | 45855.3765 | 2025-07-17 09:10 | 45855.3821 | 0.13244 | 0.016452 | 594 | 4781.7 | Unplanned | Human Error | # Line Tripped during Planned Job, Feeder 181182, Mill Lane, Kerikeri
344 |  | INCD-33527-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2025-07-17 09:02 | 45855.3765 | 2025-07-17 09:11 | 45855.383 | 0.068283 | 0.0073953 | 267 | 2465.3 | Unplanned | Human Error | # Line Tripped during Planned Job, Shepherd Rd Feeder , Mill Lane, Kerikeri
345 |  | INCD-33533-F-HONE HEKE ROAD | Kerikeri 181182 - Hone Heke Road |  | HONE HEKE ROAD | 2025-07-17 14:55 | 45855.6214 | 2025-07-17 16:24 | 45855.6832 | 1.2338 | 0.016452 | 594 | 44546.4 | Unplanned | Vegetation | # Tree on Line, Pole 401475, Honeheke Rd, Kerikeri
346 |  | INCD-33554-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-07-17 15:48 | 45855.6582 | 2025-07-17 18:07 | 45855.7552 | 1.2034 | 0.008614 | 311 | 43446.7 | Unplanned | Adverse Weather | # Sectionaliser S1003 Tripped, Runaruna Rd, Okahu Rd
347 |  | INCD-33557-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-07-17 16:21 | 45855.6813 | 2025-07-18 14:56 | 45856.6222 | 5.3591 | 0.0048194 | 174 | 193484 | Unplanned | Defective Equipment | # Replace Crossarm, Repair Conductor, Poles 413599 to 413601, Far North Rd, Pukenui
348 |  | INCD-33563-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-07-17 17:39 | 45855.7354 | 2025-07-17 21:02 | 45855.8764 | 0.08434 | 0.00041547 | 15 | 3045 | Unplanned | Adverse Weather | # Recloser Tripped during High Winds, R_T01301, Opahi Rd, Kawakawa
349 |  | INCD-33566-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-07-18 09:47 | 45856.4076 | 2025-07-18 10:18 | 45856.4292 | 0.0060104 | 0.00019388 | 7 | 217 | Unplanned | Adverse Weather | # Blown Fuses, at Link L153, Kohukohu Rd, Te Karae
350 |  | INCD-33569-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-07-30 09:41 | 45868.4035 | 2025-07-30 14:14 | 45868.5931 | 0.26465 | 0.00096942 | 35 | 9555 | Planned | Planned Outage | # Replaced Defective Conductor, Honeymoon Valley Rd, Peria
351 |  | INCD-33572-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-08-07 09:31 | 45876.3965 | 2025-08-07 14:20 | 45876.5972 | 0.48828 | 0.0016896 | 61 | 17629 | Planned | Planned Outage | # New Conductor, from Pole 905465 to 328524, Sandhills Rd, Ahipara
352 |  | INCD-33584-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-08-11 08:40 | 45880.3611 | 2025-08-11 14:08 | 45880.5889 | 0.86306 | 0.0026313 | 95 | 31160 | Planned | Planned Outage | # Vegetation Control, between Poles 406931, 406932, Onekura Rd, Waipapa
353 |  | INCD-33587-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-08-12 09:03 | 45881.3771 | 2025-08-12 13:21 | 45881.5563 | 0.4158 | 0.0018281 | 66 | 15012 | Planned | Planned Outage | # Replace Pole 410739, Upgrade Transformer T00221, Gill Rd, Awanui
354 |  | INCD-33590-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-08-12 09:10 | 45881.3819 | 2025-08-12 14:43 | 45881.6132 | 0.1199 | 0.00036007 | 13 | 4329 | Planned | Planned Outage | # Vegetation Control, Beyond Sectionaliser S158, Hansen Rd, Waipapa
355 |  | INCD-33596-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-08-13 09:36 | 45882.4 | 2025-08-13 15:07 | 45882.6299 | 0.52257 | 0.0015788 | 57 | 18867 | Planned | Planned Outage | # Pole Replacements 429530, Beyond Switch 318, Church Rd, Kaitaia
356 |  | INCD-33605-F-OMAUNU ROAD | Kaeo 191712 - Omaunu Rd |  | OMAUNU ROAD | 2025-08-18 09:14 | 45887.3847 | 2025-08-18 14:18 | 45887.5958 | 0.31154 | 0.0010248 | 37 | 11248 | Planned | Planned Outage | # Clear Vegetation, Beyond Link L524, Omaunu Rd, Kaeo
357 |  | INCD-33608-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-08-20 09:05 | 45889.3785 | 2025-08-20 13:45 | 45889.5729 | 0.062043 | 0.00022158 | 8 | 2240 | Planned | Planned Outage | # Vegetation Control, Beyond Pole 423246, Ruapekapeka Rd, Kawakawa
358 |  | INCD-33617-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-07-21 13:50 | 45859.5764 | 2025-07-21 13:55 | 45859.5799 | 0.0049856 | 0.00099712 | 36 | 180 | Unplanned | Defective Equipment | # Investigate Neutral Faults, Earth Test Two Transformers, T03448, Edmonds Rd, Kerikeri
359 |  | INCD-33623-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-07-21 13:37 | 45859.5674 | 2025-07-21 15:07 | 45859.6299 | 0.12713 | 0.0014126 | 51 | 4590 | Unplanned | Unknown | # Recloser Found Open, R_T01334, Pupuke Mangapa Rd, Kaeo
360 |  | INCD-33626-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-07-21 18:57 | 45859.7894 | 2025-07-21 23:14 | 45859.9679 | 3.7636 | 0.014763 | 533 | 135882.0667 | Unplanned | Third Party | # Vehicle vs Pole, Pole 414243, Recreation Rd, Kaikohe
361 |  | INCD-33629-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-08-14 23:04 | 45883.9611 | 2025-08-15 01:32 | 45884.0639 | 1.4224 | 0.0096111 | 347 | 51356 | Planned | Planned Outage | # Replace Pole 414243, Recreation Rd, Kaikohe
362 |  | INCD-33635-F-VICTORIA VALLEY | Kaitaia Transmission 151802 - Victoria Valley |  | VICTORIA VALLEY | 2025-08-15 09:35 | 45884.3993 | 2025-08-15 12:53 | 45884.5368 | 0.24579 | 0.0013572 | 49 | 8874 | Planned | Planned Outage | # Replaced Pole 428953, SH1, Kaitaia
363 |  | INCD-33644-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-07-24 12:37 | 45862.5257 | 2025-07-24 12:56 | 45862.5389 | 0.00052626 | 2.7698e-05 | 1 | 19 | Unplanned | Vegetation | # Vegetation Control, beyond Pole 412535, Mangamuka Rd, Kaikohe
364 |  | INCD-33644-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-07-24 12:37 | 45862.5257 | 2025-07-24 12:56 | 45862.5389 | 0.036838 | 0.0019388 | 70 | 1330 | Unplanned | Vegetation | # Vegetation Control, beyond Pole 412535, Mangamuka Rd, Kaikohe
365 |  | INCD-33653-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-08-18 12:06 | 45887.5042 | 2025-08-18 14:15 | 45887.5938 | 0.15364 | 0.001191 | 43 | 5547 | Planned | Planned Outage | # Replace Pole 405078, Waikare Rd, Kawakawa
366 |  | INCD-33656-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-08-19 09:03 | 45888.3773 | 2025-08-19 16:21 | 45888.681 | 0.22545 | 0.00088633 | 32 | 8139.7333 | Planned | Planned Outage | # Replace Cable between L487 and Switch 316, Omanaia Rd, Omanaia
367 |  | INCD-33659-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-08-19 09:52 | 45888.4111 | 2025-08-19 13:08 | 45888.5472 | 0.14115 | 0.00072014 | 26 | 5096 | Planned | Planned Outage | # Replace Pole 423632, beyond Link L954, Matawaia Maromaku Rd, Kawakawa
368 |  | INCD-33662-F-KERIKERI ROAD | Kerikeri 181112 - Kerikeri Road |  | KERIKERI ROAD | 2025-08-20 10:02 | 45889.4181 | 2025-08-20 14:31 | 45889.6049 | 0.28313 | 0.0010525 | 38 | 10222 | Planned | Planned Outage | # Replace Pole 436136, Hall Rd, Kerikeri
369 |  | INCD-33665-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-08-20 09:35 | 45889.3993 | 2025-08-20 13:07 | 45889.5465 | 0.20951 | 0.0010248 | 37 | 7564 | Planned | Planned Outage | # Replace Pole 432605, New Transformer T03120, Houhora Heads Rd, Pukenui
370 |  | INCD-33680-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2025-07-27 12:05 | 45865.5035 | 2025-07-27 15:59 | 45865.666 | 0.25061 | 0.02166 | 782 | 9048 | Unplanned | Defective Equipment | # LV Fault on Transformer T05445 Tripped HV Fuse 1042, Russell Rd, Haruru
371 |  | INCD-33683-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-07-28 13:51 | 45866.5769 | 2025-07-28 17:29 | 45866.7285 | 0.70144 | 0.0032129 | 116 | 25324.7333 | Unplanned | Third Party | # Car vs Pole, 11 kV Outage, Pole 402287, SH1, Kaikohe
372 |  | INCD-33689-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-07-28 22:40 | 45866.9446 | 2025-07-29 13:13 | 45867.5504 | 1.9135 | 0.010359 | 374 | 69085.3333 | Unplanned | Defective Equipment | # CHURCH ROAD, 11kV RECL R656, Kaitaia
373 |  | INCD-33695-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-07-28 22:50 | 45866.9516 | 2025-07-29 11:10 | 45867.4653 | 0.66175 | 0.03008 | 999.6545 | 23892 | Unplanned | Vegetation | # Tree in Line, at Pole 433472, Rakauwahia Rd, Taheke
374 |  | INCD-33695-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-07-28 22:50 | 45866.9516 | 2025-07-29 11:10 | 45867.4653 | 3.8177 | 0.017477 | 580.8306 | 137835.95 | Unplanned | Vegetation | # Tree in Line, at Pole 433472, Rakauwahia Rd, Taheke
375 |  | INCD-33695-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-07-28 22:50 | 45866.9516 | 2025-07-29 11:10 | 45867.4653 | 0.0097496 | 0.010941 | 363.5944 | 352 | Unplanned | Vegetation | # Tree in Line, at Pole 433472, Rakauwahia Rd, Taheke
376 |  | INCD-33695-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-07-28 22:50 | 45866.9516 | 2025-07-29 11:10 | 45867.4653 | 0.00060935 | 2.7698e-05 | 0.92049 | 22 | Unplanned | Vegetation | # Tree in Line, at Pole 433472, Rakauwahia Rd, Taheke
377 |  | INCD-33698-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-07-28 22:40 | 45866.9444 | 2025-07-29 11:51 | 45867.4938 | 5.8227 | 0.010581 | 304 | 210224 | Unplanned | Vegetation | # Tree Through Line, Pole 334573, Te Ahu Ahu Rd, Kaikohe
378 |  | INCD-33701-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-07-29 00:13 | 45867.009 | 2025-07-29 12:34 | 45867.524 | 2.523 | 0.0052072 | 188 | 91091.2 | Unplanned | Defective Equipment | # Failed Insulator, Pole 418823, Fairburn Rd, Taipa
379 |  | INCD-33704-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-07-29 02:24 | 45867.0998 | 2025-07-29 11:39 | 45867.4854 | 2.0083 | 0.0054288 | 196 | 72506.9 | Unplanned | Defective Equipment | # Line Down between 409155 and 332236, during Adverse Weather, Waiare Rd, Waipapa
380 |  | INCD-33716-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-07-29 06:15 | 45867.2605 | 2025-07-29 12:47 | 45867.5324 | 0.67385 | 0.01709 | 290 | 24328.7333 | Unplanned | Defective Equipment | # Faulty Bus Coupler, Ring Main RM102, Rangiahoua Rd, Waipapa
381 |  | INCD-33722-F-KAWAKAWA | Kawakawa CB0207 - Kawakawa |  | KAWAKAWA | 2025-07-29 07:45 | 45867.3232 | 2025-07-29 08:47 | 45867.366 | 0.6857 | 0.011135 | 402 | 24756.5 | Unplanned | Adverse Weather | # Circuit Breaker CB0207 Tripped during Adverse Weather, Kawakawa
382 |  | INCD-33737-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2025-07-29 12:17 | 45867.5115 | 2025-07-29 13:43 | 45867.5717 | 0.64345 | 0.007423 | 268 | 23231.1333 | Unplanned | Vegetation | # Vegetation Tripped Line at Pole 439824, Titore Way, Russell
383 |  | INCD-33746-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-07-29 11:01 | 45867.459 | 2025-07-29 16:17 | 45867.6785 | 0.07002 | 0.00022158 | 8 | 2528 | Unplanned | Unknown | # Blown Fuse L170, McIntyre Rd, Oromahoe, Mt Pokaka
384 |  | INCD-33749-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2025-07-29 15:42 | 45867.6542 | 2025-07-29 17:17 | 45867.7199 | 0.70209 | 0.007423 | 268 | 25348.3333 | Unplanned | Unknown | # Sectionaliser S1024 Tripped, During High Winds, Beresford Street, Russell
385 |  | INCD-33755-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-08-06 09:32 | 45875.3972 | 2025-08-06 13:25 | 45875.559 | 0.09035 | 0.00038777 | 14 | 3262 | Planned | Planned Outage | # Replace Pole 418901, Paranui Rd, Taipa
386 |  | INCD-33758-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-07-30 07:55 | 45868.3299 | 2025-07-30 15:16 | 45868.6361 | 0.53745 | 0.0012187 | 44 | 19404 | Unplanned | Defective Equipment | # Lines Down at Pole 414557, West Coast Rd, Okahu Rd
387 |  | INCD-33770-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-07-30 22:26 | 45868.9347 | 2025-07-31 00:28 | 45869.0197 | 0.10171 | 0.00083093 | 30 | 3672 | Unplanned | Wildlife | # Possum at Pole 407282 Tripped Sectionaliser S1046, Broadwood Rd, Okahu Rd
388 |  | INCD-33773-F-KAIKOHE | Kaikohe CB0107 - Kaikohe |  | KAIKOHE | 2025-08-08 03:07 | 45877.1299 | 2025-08-08 03:29 | 45877.1451 | 0.058498 | 0.002659 | 96 | 2112 | Planned | Planned Outage | # Network Reconfiguration, Beyond Switch 255, Station Rd, Kaikohe
389 |  | INCD-33791-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-08-12 09:02 | 45881.3764 | 2025-08-12 13:04 | 45881.5444 | 0.026811 | 0.00011079 | 4 | 968 | Planned | Planned Outage | # Tree Felling, near Pole 434526, Wharekawa Rd, Omanaia
390 |  | INCD-33800-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-08-19 09:31 | 45888.3965 | 2025-08-19 14:02 | 45888.5847 | 0.59492 | 0.0022158 | 80 | 21479 | Planned | Planned Outage | # Installed New Feeder Interconnection, at Switch 504, Sandhills Rd, Ahipara
391 |  | INCD-33806-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2025-08-25 09:32 | 45894.3972 | 2025-08-25 12:51 | 45894.5354 | 0.63511 | 0.0034068 | 123 | 22930 | Planned | Planned Outage | # Replace Poles, Upgrade T02261, Donald Rd, Kaitaia
392 |  | INCD-33812-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-08-28 11:02 | 45897.4597 | 2025-08-28 15:20 | 45897.6389 | 0.78446 | 0.0031575 | 114 | 28322 | Planned | Planned Outage | # Replace Pole 416587, Kapiro Rd, Waipapa
393 |  | INCD-33815-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-08-04 11:15 | 45873.4689 | 2025-08-04 14:47 | 45873.616 | 1.1337 | 0.016314 | 589 | 40931.7 | Unplanned | Vegetation | # Vegetation on Line, Between Poles 406925, 406927, Onekura Rd, Waipapa
394 |  | INCD-33818-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-08-04 12:14 | 45873.5097 | 2025-08-04 12:50 | 45873.5347 | 0.0099712 | 0.00027698 | 10 | 360 | Unplanned | Vegetation | # Bamboo Contacted HV Fuse L837, SH1, Pakaraka
395 |  | INCD-33830-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-08-21 09:57 | 45890.4145 | 2025-08-21 15:56 | 45890.6642 | 0.61791 | 0.033625 | 1214 | 22308.8833 | Planned | Planned Outage | # Replace Multiple Crossarms, Between Switch 1787 and R1785, Karikari Peninsula
396 |  | INCD-33836-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-08-13 09:48 | 45882.4083 | 2025-08-13 14:59 | 45882.6243 | 0.32733 | 0.0010525 | 38 | 11818 | Planned | Planned Outage | # Pole Replacement, near Pole 414921, Rahiri Rd, Kaikohe
397 |  | INCD-33839-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-08-06 10:07 | 45875.4214 | 2025-08-06 13:32 | 45875.5641 | 0.39846 | 0.0019388 | 70 | 14386.1667 | Planned | Planned Outage | # New Connection, Beyond Sectionaliser S1018, Waiare Rd, Kaikohe
398 |  | INCD-33851-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-08-06 23:15 | 45875.9688 | 2025-08-07 10:06 | 45876.4208 | 0.072125 | 0.00011079 | 4 | 2604 | Unplanned | Vegetation | # Vegetation Blew Fuse, L852, Wharau Rd, Kerikeri Inlet
399 |  | INCD-33854-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-08-18 15:00 | 45887.6253 | 2025-08-18 16:54 | 45887.7043 | 0.29598 | 0.0026036 | 94 | 10686.2333 | Planned | Planned Outage | # Replace Crossarm on Pole 35426, SH10, Taipa
400 |  | INCD-33857-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-08-12 10:02 | 45881.4181 | 2025-08-12 12:51 | 45881.5354 | 0.14511 | 0.00085863 | 31 | 5239 | Planned | Planned Outage | # Replace Cross Arm, Pole 313733, Wharekawa Rd, Omanaia
401 |  | INCD-33863-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-08-27 09:04 | 45896.3778 | 2025-08-27 11:57 | 45896.4979 | 0.016757 | 0.0016896 | 61 | 605 | Planned | Planned Outage | # Installing Group Fuses, Multiple Sites, Okura Bay Road, Kaeo
402 |  | INCD-33869-F-MATAURI BAY | Kaeo 191732 - Matauri Bay |  | MATAURI BAY | 2025-08-29 10:10 | 45898.4236 | 2025-08-29 15:52 | 45898.6611 | 0.0068413 | 0.00052626 | 19 | 247 | Planned | Planned Outage | # Installing Group Fusing, Multiple Sites, SH10, Kaeo
403 |  | INCD-33869-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2025-08-29 10:10 | 45898.4236 | 2025-08-29 15:52 | 45898.6611 | 0.0023543 | 0.00024928 | 9 | 85 | Planned | Planned Outage | # Installing Group Fusing, Multiple Sites, SH10, Kaeo
404 |  | INCD-33878-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-08-08 17:22 | 45877.7236 | 2025-08-08 20:58 | 45877.8736 | 0.022601 | 0.00022158 | 4 | 816 | Unplanned | Vegetation | # Tree on Line at Pole 450195, Wharekawa Rd, Oue
405 |  | INCD-33881-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-08-08 19:11 | 45877.7993 | 2025-08-09 13:16 | 45878.5528 | 0.21036 | 0.00019388 | 7 | 7595 | Unplanned | Defective Equipment | # Broken Jumper at Pole 412746, Kohukohu Rd, Kaikohe
406 |  | INCD-33884-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-09-01 10:42 | 45901.4458 | 2025-09-01 14:10 | 45901.5903 | 0.33991 | 0.0016342 | 59 | 12272 | Planned | Planned Outage | # Replace Pole, Crossarm, Pole 412940, Iwitaua Rd, Kaikohe
407 |  | INCD-33893-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-09-02 09:43 | 45902.4049 | 2025-09-02 14:15 | 45902.5938 | 0.26368 | 0.00096942 | 35 | 9520 | Planned | Planned Outage | # Vegetation Control, near S001, Far North Rd, Waipapakauri
408 |  | INCD-33902-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-08-09 14:18 | 45878.5958 | 2025-08-09 17:01 | 45878.709 | 0.018059 | 0.00011079 | 4 | 652 | Unplanned | Unknown | # Recloser R_T01306 Tripped , Wharekawa Rd, Omanaia
409 |  | INCD-33905-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-08-10 08:18 | 45879.3458 | 2025-08-10 09:46 | 45879.4069 | 0.60735 | 0.0080324 | 290 | 21927.7167 | Unplanned | Vegetation | # Branch on Line, at Pole 417936, Purerua Rd, Waipapa
410 |  | INCD-33908-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-09-09 08:40 | 45909.3611 | 2025-09-09 11:05 | 45909.4618 | 0.4458 | 0.0030745 | 111 | 16095 | Planned | Planned Outage | # Vegetation Control, Pole 430963, Kaimaumau Rd, Pukenui
411 |  | INCD-33911-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-09-09 09:30 | 45909.3958 | 2025-09-09 13:35 | 45909.566 | 0.047502 | 0.00019388 | 7 | 1715 | Planned | Planned Outage | # Maintain Poles 432430, 432431, 432425, 432426, Turk Valley Rd, Pukenui
412 |  | INCD-33929-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2025-09-02 09:19 | 45902.3882 | 2025-09-02 16:16 | 45902.6778 | 0.1848 | 0.00044316 | 16 | 6672 | Planned | Planned Outage | # Pole Replacement, near Sectionaliser S164, SH10, Kaeo
413 |  | INCD-33950-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-08-28 09:30 | 45897.396 | 2025-08-28 12:07 | 45897.5048 | 2.0093 | 0.012824 | 463 | 72544.3833 | Planned | Planned Outage | # Replace Pole 418257, Install Generator Links, Inland Rd, Karikari
414 |  | INCD-33953-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-08-16 14:31 | 45885.6049 | 2025-08-16 21:16 | 45885.8861 | 0.45934 | 0.001191 | 43 | 16584 | Unplanned | Defective Equipment | # Conductor Down Between Poles 345582 - 906964, Waihaha Rd, Kawakawa
415 |  | INCD-33956-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-08-17 12:09 | 45886.5062 | 2025-08-17 15:31 | 45886.6465 | 0.02238 | 0.00011079 | 4 | 808 | Unplanned | Third Party | # Car vs Pole, at Pole 450492, SH12, Rawene
416 |  | INCD-33959-F-OMAUNU ROAD | Kaeo 191712 - Omaunu Rd |  | OMAUNU ROAD | 2025-09-02 12:01 | 45902.5007 | 2025-09-02 12:33 | 45902.5229 | 0.0017727 | 5.5396e-05 | 2 | 64 | Planned | Planned Outage | # Group Fusing, Transformer T03765, Waiare Rd, Kaeo
417 |  | INCD-33977-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-08-19 12:37 | 45888.5254 | 2025-08-20 14:45 | 45889.6146 | 0.0027384 | 2.7698e-05 | 0.98958 | 98.8667 | Unplanned | Defective Equipment | # Line Down at Pole 434683, Beyond Fuse F2263, Omanaia
418 |  | INCD-33977-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-08-19 12:37 | 45888.5254 | 2025-08-20 14:45 | 45889.6146 | 3.3703 | 0.029221 | 1044.0104 | 121680.3667 | Unplanned | Defective Equipment | # Line Down at Pole 434683, Beyond Fuse F2263, Omanaia
419 |  | INCD-33980-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-08-19 18:07 | 45888.7549 | 2025-08-19 21:16 | 45888.8861 | 0.099463 | 0.00052626 | 19 | 3591 | Unplanned | Vegetation | # Branch on Line, Between Poles 428040 and 428039, Far North Rd, Pukenui
420 |  | INCD-33986-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-09-03 10:04 | 45903.4194 | 2025-09-03 14:49 | 45903.6174 | 0.047363 | 0.00016619 | 6 | 1710 | Planned | Planned Outage | # Replace Pole 419853, Fuse F2071, Horeke Rd, Kaikohe
421 |  | INCD-33998-F-TI BAY | Haruru CB0606 - Ti Bay |  | TI BAY | 2025-09-05 09:01 | 45905.3754 | 2025-09-05 13:32 | 45905.5636 | 2.4096 | 0.008891 | 321 | 86996.35 | Planned | Planned Outage | # Install New Poles, near 735, Puketona Rd, Haruru
422 |  | INCD-34010-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-09-10 09:41 | 45910.4035 | 2025-09-10 13:15 | 45910.5521 | 0.082982 | 0.00038777 | 14 | 2996 | Planned | Planned Outage | # New Pole near Pole 30470, Rangikohu Rd, Kaitaia
423 |  | INCD-34019-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-09-03 09:28 | 45903.3948 | 2025-09-03 14:27 | 45903.6021 | 2.6352 | 0.032046 | 1157 | 95140.8667 | Planned | Planned Outage | # Replace Poles, near 418073, Inland Rd, Taipa
424 |  | INCD-34022-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-09-10 10:03 | 45910.4187 | 2025-09-10 15:39 | 45910.6521 | 1.3176 | 0.010193 | 184 | 47572 | Planned | Planned Outage | # Replace Poles 405821 & 405826, Transformer T04176, Omanaia
425 |  | INCD-34028-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-09-11 09:04 | 45911.3778 | 2025-09-11 12:15 | 45911.5104 | 0.099075 | 0.00052626 | 19 | 3577 | Planned | Planned Outage | # Replace Pole 431195, SH1, Kaikohe
426 |  | INCD-34034-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-09-15 11:25 | 45915.4757 | 2025-09-15 14:21 | 45915.5979 | 0.77509 | 0.0044039 | 159 | 27984 | Planned | Planned Outage | # Upgrade Transformer T02325, Quarry Rd, Kaikohe
427 |  | INCD-34037-F-POKAPU | Moerewa 031312 - Pokapu |  | POKAPU | 2025-09-05 10:10 | 45905.4236 | 2025-09-05 14:03 | 45905.5854 | 0.067444 | 0.00030468 | 11 | 2435 | Planned | Planned Outage | # Re-Sag Lines, near Transformer T01014, Ngawhitu Rd, Moerewa
428 |  | INCD-34040-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-09-09 09:48 | 45909.4083 | 2025-09-09 17:28 | 45909.7278 | 0.26147 | 0.00072014 | 26 | 9440 | Planned | Planned Outage | # Replace Poles 438726 to 438723, Signal Station Rd, Omanaia
429 |  | INCD-34049-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-08-24 06:13 | 45893.2588 | 2025-08-24 11:25 | 45893.4757 | 0.0031635 | 2.6555e-05 | 0.95874 | 114.2167 | Unplanned | Defective Equipment | # Line Down at Pole 434683, Koutu Loop Rd, Omanaia
430 |  | INCD-34049-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-08-24 06:13 | 45893.2588 | 2025-08-24 11:25 | 45893.4757 | 3.2022 | 0.030219 | 1091.0413 | 115610.55 | Unplanned | Defective Equipment | # Line Down at Pole 434683, Koutu Loop Rd, Omanaia
431 |  | INCD-34061-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-08-25 08:37 | 45894.359 | 2025-08-25 12:00 | 45894.5 | 0.039359 | 0.00019388 | 7 | 1421 | Unplanned | Defective Equipment | # Replace Crossarm, at Pole 400860, Kerikeri Inlet Rd, Kerikeri
432 |  | INCD-34067-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-09-12 09:32 | 45912.3972 | 2025-09-12 13:14 | 45912.5514 | 1.0896 | 0.0075892 | 274 | 39340.0833 | Planned | Planned Outage | # Network Additions, Near Pole 424493, Fosters Rd, Taipa
433 |  | INCD-34079-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-09-16 09:38 | 45916.4014 | 2025-09-16 12:56 | 45916.5389 | 0.010968 | 5.5396e-05 | 2 | 396 | Planned | Planned Outage | # Replace Poles, near Link L074, West Coast Rd, Okau Rd
434 |  | INCD-34082-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-08-26 09:31 | 45895.3967 | 2025-08-26 14:15 | 45895.5938 | 1.1037 | 0.0042101 | 152 | 39848.2667 | Planned | Planned Outage | # Replacing Poles 421231, 418125, Cross Arms, Beyond Links L1062, Rangiputa, Taipa
435 |  | INCD-34085-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-09-04 09:31 | 45904.3963 | 2025-09-04 14:54 | 45904.6208 | 3.1379 | 0.010331 | 373 | 113291.0667 | Planned | Planned Outage | # Network Upgrade, Near Switch 1374M, Inland Rd, Taipa
436 |  | INCD-34091-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-09-17 09:24 | 45917.3917 | 2025-09-17 15:01 | 45917.6257 | 0.23621 | 0.00072014 | 26 | 8528 | Planned | Planned Outage | # Replace Poles 438718 to 438731, SH12, Omanaia
437 |  | INCD-34094-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-09-18 09:35 | 45918.3993 | 2025-09-18 13:36 | 45918.5667 | 0.033376 | 0.00013849 | 5 | 1205 | Planned | Planned Outage | # Replace Poles 414687 to 414727, West Coast Rd, Panguru
438 |  | INCD-34109-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-08-28 12:57 | 45897.5396 | 2025-08-28 15:02 | 45897.6264 | 0.048471 | 0.00038777 | 14 | 1750 | Unplanned | Unknown | # HV Fuse F2013 Operated, Auckland Block Rd, Omanaia
439 |  | INCD-34115-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-08-28 15:03 | 45897.6271 | 2025-08-28 19:15 | 45897.8021 | 0.069798 | 0.00027698 | 10 | 2520 | Unplanned | Defective Equipment | # Blown Jumper on Pole 435187, Mangapupu Rd, Omanaia
440 |  | INCD-34136-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-09-16 10:07 | 45916.4215 | 2025-09-16 11:35 | 45916.4826 | 0.034124 | 0.00038777 | 14 | 1232 | Planned | Planned Outage | # Repair Conductor Between Poles 413315 & 202423, Auckland Block Rd, Omanaia
441 |  | INCD-34139-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-09-22 10:40 | 45922.4444 | 2025-09-22 13:28 | 45922.5611 | 0.055839 | 0.00033237 | 12 | 2016 | Planned | Planned Outage | # Upgrade Transformer T03496, Totara School Rd, Kaeo
442 |  | INCD-34142-F-KAIKOHE | Kaikohe CB0107 - Kaikohe |  | KAIKOHE | 2025-09-22 22:01 | 45922.9174 | 2025-09-22 22:17 | 45922.9285 | 0.042544 | 0.002659 | 96 | 1536 | Planned | Planned Outage | # Install new Fuses, at T05046, Station Rd, Kaikohe
443 |  | INCD-34145-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-09-18 09:31 | 45918.3965 | 2025-09-18 13:20 | 45918.5556 | 0.36453 | 0.0018281 | 66 | 13161 | Planned | Planned Outage | # Maintain Transformer T02540, Gill Rd, Kaitaia
444 |  | INCD-34148-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-09-23 09:39 | 45923.4021 | 2025-09-23 13:51 | 45923.5771 | 0.30711 | 0.0012187 | 44 | 11088 | Planned | Planned Outage | # Pole Replacement 414564 to 414636, West Coast Rd, Kaitaia
445 |  | INCD-34163-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-08-29 16:33 | 45898.6896 | 2025-08-30 16:25 | 45899.684 | 0.39406 | 0.00030468 | 11 | 14227 | Unplanned | Defective Equipment | # Broken HV Jumper, Pole 434740, Brindle Rd, Omanaia
446 |  | INCD-34169-F-OMAUNU ROAD | Kaeo 191712 - Omaunu Rd |  | OMAUNU ROAD | 2025-08-30 14:00 | 45899.5833 | 2025-08-30 19:07 | 45899.7965 | 0.1142 | 0.0010248 | 37 | 4123 | Unplanned | Defective Equipment | # Replaced SWER Transformer T04458, Omaunu Rd, Kaeo
447 |  | INCD-34181-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-08-31 08:28 | 45900.3528 | 2025-08-31 14:34 | 45900.6069 | 0.28119 | 0.00091403 | 33 | 10152 | Unplanned | Defective Equipment | # Defective Transformer, Honeymoon Valley Rd, Taipa
448 |  | INCD-34190-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-08-31 11:36 | 45900.4833 | 2025-09-01 12:18 | 45901.5125 | 0.2541 | 0.0011356 | 41 | 9174 | Unplanned | Defective Equipment | # Repair Transformer T03130, Waiotemarama Gorge Rd, Omanaia
449 |  | INCD-34202-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-08-31 15:41 | 45900.6533 | 2025-08-31 19:54 | 45900.8292 | 1.7755 | 0.014652 | 529 | 64102.8667 | Unplanned | Unknown | # Sectionaliser S1003 Opened during Adverse Weather, RunaRuna Rd, Broadwood
450 |  | INCD-34211-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-08-31 16:00 | 45900.6667 | 2025-08-31 20:28 | 45900.8531 | 0.22418 | 0.0020496 | 45.9392 | 8093.75 | Unplanned | Unknown | # Recloser Tripped during High Winds, R426, Kaitaia
451 |  | INCD-34211-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2025-08-31 16:00 | 45900.6667 | 2025-08-31 20:28 | 45900.8531 | 0.084824 | 0.00077554 | 17.3824 | 3062.5 | Unplanned | Unknown | # Recloser Tripped during High Winds, R426, Kaitaia
452 |  | INCD-34211-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-08-31 16:00 | 45900.6667 | 2025-08-31 20:28 | 45900.8531 | 1.1227 | 0.0041824 | 93.7408 | 40533.4333 | Unplanned | Unknown | # Recloser Tripped during High Winds, R426, Kaitaia
453 |  | INCD-34211-F-VICTORIA VALLEY | Kaitaia Transmission 151802 - Victoria Valley |  | VICTORIA VALLEY | 2025-08-31 16:00 | 45900.6667 | 2025-08-31 20:28 | 45900.8531 | 1.127 | 0.010304 | 230.9376 | 40687.5 | Unplanned | Unknown | # Recloser Tripped during High Winds, R426, Kaitaia
454 |  | INCD-34214-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-08-31 16:04 | 45900.6692 | 2025-08-31 21:03 | 45900.8771 | 1.4927 | 0.016813 | 607 | 53893.0667 | Unplanned | Vegetation | # Remove Vegetation From Lines, at Pole 440375, SH10, Waipapa
455 |  | INCD-34217-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-08-31 16:42 | 45900.696 | 2025-09-01 22:14 | 45901.9266 | 4.5306 | 0.044178 | 1176 | 163572.7667 | Unplanned | Defective Equipment | # Blown Jumper, due to Lightning Strike, Near Switch 747, Taipa
456 |  | INCD-34223-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-08-31 16:36 | 45900.6915 | 2025-08-31 19:20 | 45900.8056 | 0.66739 | 0.010359 | 374 | 24095.5667 | Unplanned | Defective Equipment | # Broken Binder, at Pole 429260, Church Rd, Kaingaroa
457 |  | INCD-34229-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-08-31 17:00 | 45900.7084 | 2025-08-31 21:42 | 45900.9042 | 2.7333 | 0.0096942 | 350 | 98682.5 | Unplanned | Defective Equipment | # Floating Conductor, at Pole 435633, Far North Rd, Pukenui
458 |  | INCD-34235-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-08-31 14:21 | 45900.5979 | 2025-08-31 17:56 | 45900.7472 | 0.07146 | 0.00033237 | 12 | 2580 | Unplanned | Unknown | # Blown Fuse F2303 during Adverse Weather, Totara North Rd, Kaeo
459 |  | INCD-34241-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-08-31 22:10 | 45900.9236 | 2025-09-01 13:50 | 45901.5764 | 0.26036 | 0.00027698 | 10 | 9400 | Unplanned | Defective Equipment | # Line Down during Adverse Weather, Pole 434525, Wharekawa Rd, Omanaia
460 |  | INCD-34244-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-09-01 08:48 | 45901.3667 | 2025-09-01 13:28 | 45901.5611 | 0.05631 | 0.00038777 | 14 | 2033 | Unplanned | Vegetation | # Recloser R_T01333, Hapanga Rd, Kaikohe
461 |  | INCD-34253-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-09-01 09:59 | 45901.416 | 2025-09-01 11:17 | 45901.4701 | 0.090738 | 0.0011633 | 42 | 3276 | Unplanned | Defective Equipment | # Broken Crossarm, Pole 428656, Unahi Rd, Kaitaia
462 |  | INCD-34256-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-09-01 10:03 | 45901.4187 | 2025-09-02 13:05 | 45902.5451 | 0.53052 | 0.0023266 | 31 | 19154 | Unplanned | Vegetation | # Tree vs Line, beyond R_T01325, West Coast Rd, Kaikohe
463 |  | INCD-34268-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-09-01 14:15 | 45901.5938 | 2025-09-01 17:14 | 45901.7181 | 0.16504 | 0.0096942 | 350 | 5958.6 | Unplanned | Vegetation | # Two Lines Down, Near Pole 431822, Te Ahu Rd, Te Kao, Pukenui
464 |  | INCD-34271-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-09-01 15:15 | 45901.6354 | 2025-09-01 19:41 | 45901.8201 | 0.15702 | 0.0027698 | 58 | 5669 | Unplanned | Unknown | # Circuit Breaker Tripped CB41632, Rangihoua Rd, Waipapa
465 |  | INCD-34277-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-09-01 17:55 | 45901.7464 | 2025-09-01 23:18 | 45901.9708 | 0.83829 | 0.030329 | 607 | 30265.6833 | Unplanned | Defective Equipment | # Line Down, Pole 437076, Somerville Rd, Waipapa
466 |  | INCD-34280-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-09-01 18:33 | 45901.7731 | 2025-09-01 19:31 | 45901.8132 | 0.41366 | 0.016536 | 597 | 14934.95 | Unplanned | Unknown | # 33kV CHT-PKN Tripped, Pukenui Substation
467 |  | INCD-34280-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-09-01 18:33 | 45901.7731 | 2025-09-01 19:31 | 45901.8132 | 0.81253 | 0.018558 | 670 | 29335.6 | Unplanned | Unknown | # 33kV CHT-PKN Tripped, Pukenui Substation
468 |  | INCD-34289-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2025-09-16 09:14 | 45916.3847 | 2025-09-16 15:23 | 45916.641 | 0.10802 | 0.0028252 | 102 | 3900 | Planned | Planned Outage | # Fusing Project, Multiple Sites, CB1122 Feeder, Mt Pokaka
469 |  | INCD-34310-F-PUKEPOTO | Okahu CB1110 - Pukepoto |  | PUKEPOTO | 2025-09-17 13:31 | 45917.5632 | 2025-09-17 14:27 | 45917.6021 | 0.071349 | 0.0012741 | 46 | 2576 | Planned | Planned Outage | # Routine Maintenance RM111, near Switch 1020, Worth Street, Kaitaia
470 |  | INCD-34319-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-09-04 13:02 | 45904.5431 | 2025-09-04 14:37 | 45904.609 | 0.28418 | 0.0029914 | 108 | 10260 | Unplanned | Defective Equipment | # Repair Strain Insulator, Pole 417562, Pawarenga Rd, Kaitaia
471 |  | INCD-34325-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-09-17 09:38 | 45917.4014 | 2025-09-17 14:17 | 45917.5951 | 0.3314 | 0.0020773 | 75 | 11965 | Planned | Planned Outage | # Maitanance Multiple Devices, near Link L421, Tokerau Beach Rd, Taipa
472 |  | INCD-34334-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-09-04 17:28 | 45904.7278 | 2025-09-04 21:13 | 45904.884 | 0.15087 | 0.0040439 | 95 | 5446.85 | Unplanned | Defective Equipment | # Crossarm Replaced, near Transformer T04489, Far North Rd, Pukenui
473 |  | INCD-34340-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-09-06 06:00 | 45906.25 | 2025-09-06 08:15 | 45906.3438 | 0.12713 | 0.00094172 | 34 | 4590 | Unplanned | Vegetation | # Vegetation on Line, Pole 435738, Kimberley Rd, Pukenui
474 |  | INCD-34343-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-09-18 22:03 | 45918.9187 | 2025-09-19 02:16 | 45919.0947 | 4.4772 | 0.022934 | 828 | 161646 | Planned | Planned Outage | # Install Recloser 033, near Pole 426947, Turvey Rd, Taipa
475 |  | INCD-34346-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-09-26 11:58 | 45926.4986 | 2025-09-26 13:58 | 45926.5819 | 0.24152 | 0.0022158 | 80 | 8720 | Planned | Planned Outage | # Install Pole 437126, Wainui Rd, Mahinepua
476 |  | INCD-34349-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-10-01 09:01 | 45931.3756 | 2025-10-01 15:00 | 45931.625 | 0.31825 | 0.00088633 | 32 | 11490.1333 | Planned | Planned Outage | # Planned Maintenance on Rawene Feeder, SH12, Omanaia
477 |  | INCD-34364-F-HONE HEKE ROAD | Kerikeri 181182 - Hone Heke Road |  | HONE HEKE ROAD | 2025-09-25 09:13 | 45925.384 | 2025-09-25 15:27 | 45925.6438 | 0.014708 | 0.0016342 | 59 | 531 | Planned | Planned Outage | # Group Fusing Project, Multiple Location, Inlet Rd Feeder, Kerikeri
478 |  | INCD-34364-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2025-09-25 09:13 | 45925.384 | 2025-09-25 15:27 | 45925.6438 | 0.015954 | 0.00091403 | 33 | 576 | Planned | Planned Outage | # Group Fusing Project, Multiple Location, Inlet Rd Feeder, Kerikeri
479 |  | INCD-34364-F-KERIKERI ROAD | Kerikeri 181112 - Kerikeri Road |  | KERIKERI ROAD | 2025-09-25 09:13 | 45925.384 | 2025-09-25 15:27 | 45925.6438 | 0.0035176 | 0.00049856 | 18 | 127 | Planned | Planned Outage | # Group Fusing Project, Multiple Location, Inlet Rd Feeder, Kerikeri
480 |  | INCD-34364-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-09-25 09:13 | 45925.384 | 2025-09-25 15:27 | 45925.6438 | 0.047557 | 0.0039885 | 144 | 1717 | Planned | Planned Outage | # Group Fusing Project, Multiple Location, Inlet Rd Feeder, Kerikeri
481 |  | INCD-34373-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-10-01 10:00 | 45931.4167 | 2025-10-01 13:08 | 45931.5472 | 0.03645 | 0.00019388 | 7 | 1316 | Planned | Planned Outage | # HV Alterations at Transformer T02094, Bullman Rd, Kaikohe
482 |  | INCD-34376-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-10-02 09:32 | 45932.3972 | 2025-10-02 13:37 | 45932.5674 | 0.088217 | 0.00036007 | 13 | 3185 | Planned | Planned Outage | # Replace Crossarms, On Poles 426863 to 426876, Cable Bay, Coopers Beach
483 |  | INCD-34379-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-09-07 16:59 | 45907.7076 | 2025-09-07 18:45 | 45907.7812 | 0.30828 | 0.0029083 | 105 | 11130 | Unplanned | Defective Equipment | # Replace Crossarm, Switch 623, Otaua Rd, Omanaia
484 |  | INCD-34385-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-09-18 23:39 | 45918.9854 | 2025-09-19 02:31 | 45919.1046 | 1.9051 | 0.011091 | 400.4411 | 68783.4049 | Planned | Planned Outage | # Maintain Ring Main RM054, Paewhenua Island, Taipa
485 |  | INCD-34385-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-09-18 23:39 | 45918.9854 | 2025-09-19 02:31 | 45919.1046 | 0.5172 | 0.0038932 | 140.5589 | 18672.8951 | Planned | Planned Outage | # Maintain Ring Main RM054, Paewhenua Island, Taipa
486 |  | INCD-34388-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-09-26 09:41 | 45926.4035 | 2025-09-26 13:30 | 45926.5625 | 0.0444 | 0.00019388 | 7 | 1603 | Planned | Planned Outage | # Pole Replacement, Pole 434453, Gammon Rd, Awarua
487 |  | INCD-34391-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-09-08 07:53 | 45908.3285 | 2025-09-08 10:50 | 45908.4514 | 0.009805 | 5.5396e-05 | 2 | 354 | Unplanned | Unknown | # Replace Fuses, near Link L488, Sandhills Rd, Kaitaia
488 |  | INCD-34397-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-09-08 12:27 | 45908.5188 | 2025-09-08 13:54 | 45908.5792 | 0.060243 | 0.00069244 | 25 | 2175 | Unplanned | Third Party | # Replace Broken Fuse L003, Kerikeri Inlet Rd, Kerikeri
489 |  | INCD-34400-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-09-08 15:34 | 45908.6486 | 2025-09-08 19:29 | 45908.8118 | 0.097635 | 0.00041547 | 15 | 3525 | Unplanned | Defective Equipment | # Defective Recloser R_T01280, Gill Rd, Kaitaia
490 |  | INCD-34418-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-09-24 10:05 | 45924.4201 | 2025-09-24 12:29 | 45924.5201 | 0.032656 | 0.00027698 | 10 | 1179 | Planned | Planned Outage | # 6212 : Ngapuhi Rd T01724 : Fault Prevention
491 |  | INCD-34433-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-09-11 09:33 | 45911.3979 | 2025-09-11 11:16 | 45911.4694 | 0.20826 | 0.0020219 | 73 | 7519 | Planned | Planned Outage | # Remove Tree, Pole 421655, Oruru Rd, Taipa
492 |  | INCD-34436-F-TI BAY | Haruru CB0606 - Ti Bay |  | TI BAY | 2025-09-18 09:04 | 45918.3778 | 2025-09-18 14:41 | 45918.6118 | 0.020884 | 0.001191 | 43 | 754 | Planned | Planned Outage | # Fusing Project, Multiple Site, Puketona Rd, Haruru
493 |  | INCD-34436-F-ONEWHERO | Haruru CB0608 - Onewhero |  | ONEWHERO | 2025-09-18 09:04 | 45918.3778 | 2025-09-18 14:41 | 45918.6118 | 0.0249 | 0.00085863 | 31 | 899 | Planned | Planned Outage | # Fusing Project, Multiple Site, Puketona Rd, Haruru
494 |  | INCD-34436-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2025-09-18 09:04 | 45918.3778 | 2025-09-18 14:41 | 45918.6118 | 0.012963 | 0.0014403 | 52 | 468 | Planned | Planned Outage | # Fusing Project, Multiple Site, Puketona Rd, Haruru
495 |  | INCD-34436-F-PUKETONA | Haruru CB0607 - Puketona |  | PUKETONA | 2025-09-18 09:04 | 45918.3778 | 2025-09-18 14:41 | 45918.6118 | 0.1761 | 0.0051518 | 186 | 6358 | Planned | Planned Outage | # Fusing Project, Multiple Site, Puketona Rd, Haruru
496 |  | INCD-34448-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-10-02 09:31 | 45932.3967 | 2025-10-02 16:19 | 45932.6799 | 1.8091 | 0.0045424 | 164 | 65316.1 | Planned | Planned Outage | # Replace Poles 426944, 426943 and 426941, Turvey Rd, Taipa
497 |  | INCD-34454-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-10-08 09:32 | 45938.3972 | 2025-10-08 14:03 | 45938.5854 | 0.57102 | 0.0022158 | 80 | 20616 | Planned | Planned Outage | # Replace Pole 410751, Sandhills Rd, Kaitaia
498 |  | INCD-34457-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-09-11 06:04 | 45911.2529 | 2025-09-11 14:31 | 45911.6049 | 0.0041814 | 2.7698e-05 | 1 | 150.9667 | Unplanned | Defective Equipment | # Faulty Transformer T00077, SH1, Mangamuka, Kaikohe
499 |  | INCD-34457-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-09-11 06:04 | 45911.2529 | 2025-09-11 14:31 | 45911.6049 | 1.1412 | 0.0078662 | 284 | 41201.5833 | Unplanned | Defective Equipment | # Faulty Transformer T00077, SH1, Mangamuka, Kaikohe
500 |  | INCD-34460-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-09-11 13:09 | 45911.5479 | 2025-09-11 14:44 | 45911.6139 | 0.039469 | 0.00041547 | 15 | 1425 | Unplanned | Defective Equipment | # Replace Fuse Saver, near Transformer T01280, Gill Rd, Awanui
501 |  | INCD-34469-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-10-09 09:32 | 45939.3972 | 2025-10-09 13:47 | 45939.5743 | 0.034899 | 0.00013849 | 5 | 1260 | Planned | Planned Outage | # Replace Poles 427419 to 427425, Ngakaroa Rd, Ahipara
502 |  | INCD-34472-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-10-10 09:39 | 45940.4021 | 2025-10-10 12:55 | 45940.5382 | 0.027144 | 0.00013849 | 5 | 980 | Planned | Planned Outage | # Replace Crossarms, Beyond Fuse F2494, Ngakaroa Rd, Ahipara
503 |  | INCD-34487-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-09-13 14:26 | 45913.6014 | 2025-09-13 20:10 | 45913.8403 | 0.12242 | 0.00047086 | 17 | 4420 | Unplanned | Defective Equipment | # Flipped Crossarm, at Transformer T00361, Pukewhai Rd, Taipa
504 |  | INCD-34490-F-AERODROME ROAD | Waipapa 041622 - Aerodrome Rd |  | AERODROME ROAD | 2025-09-13 14:51 | 45913.6188 | 2025-09-13 16:21 | 45913.6813 | 0.4512 | 0.0050133 | 181 | 16290 | Unplanned | Vegetation | # Branch on Line, Pole 437475, during High Winds, Puketotara Rd, Waipapa
505 |  | INCD-34532-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-09-14 12:57 | 45914.5395 | 2025-09-14 17:21 | 45914.7232 | 1.0035 | 0.0037946 | 137 | 36231.9333 | Unplanned | Defective Equipment | # Repair Suspension Clamp, Pole 422616, Kohukohu Rd, Kaikohe
506 |  | INCD-34550-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-10-22 09:33 | 45952.3979 | 2025-10-22 13:54 | 45952.5792 | 0.041574 | 0.00016619 | 6 | 1501 | Planned | Planned Outage | # Replaced Poles 424118, 424126, 424130, Simmental Lane, Taipa
507 |  | INCD-34553-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-09-16 10:15 | 45916.4271 | 2025-09-16 15:48 | 45916.6583 | 0.38395 | 0.0011633 | 42 | 13862 | Unplanned | Third Party | # Replace Pole 410310, Otangroa Rd, Totara North, Kaeo
508 |  | INCD-34556-F-MATAURI BAY | Kaeo 191732 - Matauri Bay |  | MATAURI BAY | 2025-09-29 10:33 | 45929.4396 | 2025-09-29 14:41 | 45929.6118 | 0.035121 | 0.00016619 | 6 | 1268 | Planned | Planned Outage | # Replace Transformer T01006, Matauri Bay Rd, Kaeo
509 |  | INCD-34562-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-10-22 09:03 | 45952.3771 | 2025-10-22 14:48 | 45952.6167 | 0.06689 | 0.00019388 | 7 | 2415 | Planned | Planned Outage | # Vegetation Control, Beyond Sectionaliser S024, Waiotehue Rd, Herekino
510 |  | INCD-34577-F-ONEWHERO | Haruru CB0608 - Onewhero |  | ONEWHERO | 2025-09-17 19:55 | 45917.83 | 2025-09-17 20:38 | 45917.8595 | 0.011828 | 0.0002782 | 10.0442 | 427.0438 | Unplanned | Unknown | # Sectionaliser S1021 Tripped, Puketona Rd, Haruru
511 |  | INCD-34577-F-TI BAY | Haruru CB0606 - Ti Bay |  | TI BAY | 2025-09-17 19:55 | 45917.83 | 2025-09-17 20:38 | 45917.8595 | 0.52399 | 0.012324 | 444.9558 | 18918.0396 | Unplanned | Unknown | # Sectionaliser S1021 Tripped, Puketona Rd, Haruru
512 |  | INCD-34580-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2025-09-18 12:48 | 45918.5337 | 2025-09-18 12:52 | 45918.5364 | 0.014183 | 0.0036838 | 133 | 512.05 | Unplanned | Human Error | # Tree Contact, Near Recloser R458, Matarau Rd, Kaikohe
513 |  | INCD-34592-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-09-18 15:27 | 45918.6438 | 2025-09-18 18:38 | 45918.7764 | 0.23277 | 0.0012187 | 44 | 8404 | Unplanned | Unknown | # Recloser R_T01298 Tripped, West Coast Rd, Motuti
514 |  | INCD-34604-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-09-18 22:59 | 45918.9576 | 2025-09-19 00:42 | 45919.0292 | 0.045646 | 0.00044316 | 16 | 1648 | Unplanned | Wildlife | # Possum vs Line, near Pole 408783, Waihapa Rd, Kaeo
515 |  | INCD-34625-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-09-20 19:21 | 45920.8063 | 2025-09-21 11:18 | 45921.4708 | 0.82171 | 0.00085863 | 31 | 29667 | Unplanned | Defective Equipment | # Line Down, Between Poles 420471 and420475, Paponga Rd, Kaikohe
516 |  | INCD-34628-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2025-09-20 19:18 | 45920.8042 | 2025-09-20 21:24 | 45920.8917 | 0.02094 | 0.00016619 | 6 | 756 | Unplanned | Defective Equipment | # Burnt Link L156, Shepherd Rd, Kerikeri
517 |  | INCD-34631-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-10-02 09:01 | 45932.3755 | 2025-10-02 14:19 | 45932.5966 | 2.548 | 0.0080047 | 289 | 91993.3167 | Planned | Planned Outage | # Network Alterations beyond Recloser R113, Purerua Rd, Waipapa
518 |  | INCD-34634-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2025-09-21 11:17 | 45921.4703 | 2025-09-21 12:02 | 45921.5015 | 0.83665 | 0.019084 | 689 | 30206.3167 | Unplanned | Vegetation | # Circuit Breaker CB0208 Tripped, Settlement Rd, Kawakawa
519 |  | INCD-34637-F-KAIKOHE | Kaikohe CB0107 - Kaikohe |  | KAIKOHE | 2025-10-03 10:01 | 45933.4174 | 2025-10-03 13:13 | 45933.5507 | 1.9942 | 0.010387 | 375 | 72000 | Planned | Planned Outage | # HV Maintenance near T02172, Hillcrest Rd, Kaikohe
520 |  | INCD-34649-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2025-10-31 08:34 | 45961.3569 | 2025-10-31 12:27 | 45961.5188 | 0.29686 | 0.0012741 | 46 | 10718 | Planned | Planned Outage | # Vegetation Control, Pole 438486, Veronica Point Drive, Paihia
521 |  | INCD-34661-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2025-10-10 10:32 | 45940.4389 | 2025-10-10 10:57 | 45940.4563 | 0.00069244 | 2.7698e-05 | 1 | 25 | Planned | Planned Outage | # Group Fusing Project, SH10, Kaeo
522 |  | INCD-34664-F-AERODROME ROAD | Waipapa 041622 - Aerodrome Rd |  | AERODROME ROAD | 2025-10-15 14:04 | 45945.5861 | 2025-10-15 14:44 | 45945.6139 | 0.0011079 | 2.7698e-05 | 1 | 40 | Planned | Planned Outage | # Straigthen Ring Main Unit RM286, Kahikatearoa Lane, Waipapa
523 |  | INCD-34673-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-09-24 06:23 | 45924.266 | 2025-09-24 10:50 | 45924.4514 | 0.051767 | 0.00019388 | 7 | 1869 | Unplanned | Defective Equipment | # Replace Crossarm, Pole 411944, Forest Rd, Waihou Valley
524 |  | INCD-34694-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-09-24 13:58 | 45924.5819 | 2025-09-24 18:56 | 45924.7889 | 1.0945 | 0.022768 | 822 | 39516.9833 | Unplanned | Defective Equipment | # Conductor Down Between Poles 438726 and 438727, Signal Station Rd, Omapere
525 |  | INCD-34703-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-10-15 09:12 | 45945.3833 | 2025-10-15 16:50 | 45945.7014 | 0.40827 | 0.0021327 | 77 | 14740 | Planned | Planned Outage | # Vegetation ControlBeyond F2377 and Line Repair at Pole 414577, Motuti Rd, Panguru
526 |  | INCD-34715-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-09-25 06:04 | 45925.2527 | 2025-09-25 07:13 | 45925.3009 | 1.2727 | 0.018585 | 671 | 45950.7 | Unplanned | Unknown | # Pukenui Substation Tripped 33kV Line, CHT-PKN, 33kV at CB 273332, Church Rd, Kaitaia
527 |  | INCD-34715-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-09-25 06:04 | 45925.2527 | 2025-09-25 07:13 | 45925.3009 | 0.67494 | 0.016757 | 605 | 24367.9 | Unplanned | Unknown | # Pukenui Substation Tripped 33kV Line, CHT-PKN, 33kV at CB 273332, Church Rd, Kaitaia
528 |  | INCD-34733-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-10-14 10:04 | 45944.4194 | 2025-10-14 11:42 | 45944.4875 | 0.15201 | 0.0015511 | 56 | 5488 | Planned | Planned Outage | # Install Bird Scarers, Lake Rd, Kaikohe
529 |  | INCD-34742-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-10-15 09:31 | 45945.3965 | 2025-10-15 13:24 | 45945.5583 | 1.6457 | 0.0070629 | 255 | 59415 | Planned | Planned Outage | # Planned Capital Extension, Between Switches 1366 and 466, Far North Rd, Pukenui
530 |  | INCD-34751-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-09-30 09:31 | 45930.3968 | 2025-09-30 13:19 | 45930.5547 | 3.2027 | 0.023128 | 671 | 115628.75 | Planned | Planned Outage | # Replace Poles 435517, 435519, 435699, Other Hardware, Far North Rd, Te Kao
531 |  | INCD-34757-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-10-01 15:57 | 45931.6646 | 2025-10-01 18:55 | 45931.7882 | 0.019721 | 0.00011079 | 4 | 712 | Unplanned | Unknown | # Links found Open L668, Mangataraine Rd, Utakura
532 |  | INCD-34778-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-10-02 14:54 | 45932.6208 | 2025-10-02 16:15 | 45932.6771 | 0.004487 | 5.5396e-05 | 2 | 162 | Unplanned | Defective Equipment | # Crossarm Remediation, at Pole 410800, Sandhills Rd, Kaitaia
533 |  | INCD-34787-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-10-17 09:01 | 45947.3757 | 2025-10-17 14:04 | 45947.5861 | 3.2513 | 0.011135 | 402 | 117383.4333 | Planned | Planned Outage | # Install New Regulator VR09, SH1, Waiomio
534 |  | INCD-34790-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-10-21 09:36 | 45951.4 | 2025-10-21 13:59 | 45951.5826 | 0.24767 | 0.00094172 | 34 | 8942 | Planned | Planned Outage | # Vegetatoin Control, Beyond Link L044, Te Tio Road, Kaikohe
535 |  | INCD-34793-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-10-23 09:22 | 45953.3903 | 2025-10-23 15:20 | 45953.6389 | 0.067749 | 0.00019388 | 7 | 2446 | Planned | Planned Outage | # Replace Pole 423689, Upgrade Transformer T04109, Martin Rd, Kawakawa
536 |  | INCD-34799-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-10-04 12:10 | 45934.5069 | 2025-10-05 12:02 | 45935.5014 | 1.4181 | 0.0010802 | 39 | 51198 | Unplanned | Defective Equipment | # Line Down, Between Poles 418954 - 327975, Taylor Rd, Taipa
537 |  | INCD-34802-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-10-04 12:14 | 45934.5097 | 2025-10-04 14:05 | 45934.5868 | 0.02767 | 0.00024928 | 9 | 999 | Unplanned | Defective Equipment | # Blown Fuse L573, Horeke Rd, Kaikohe
538 |  | INCD-34814-F-TAU BLOCK | Moerewa 031372 - Tau Block |  | TAU BLOCK | 2025-10-05 04:24 | 45935.1834 | 2025-10-05 14:30 | 45935.6042 | 0.00096111 | 2.7698e-05 | 1 | 34.7 | Unplanned | Third Party | # Car vs Pole, at Pole 420761, George Street, Moerewa
539 |  | INCD-34814-F-MOEREWA | Moerewa 031322 - Moerewa |  | MOEREWA | 2025-10-05 04:24 | 45935.1834 | 2025-10-05 14:30 | 45935.6042 | 4.6325 | 0.015538 | 561 | 167252.6333 | Unplanned | Third Party | # Car vs Pole, at Pole 420761, George Street, Moerewa
540 |  | INCD-34817-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-10-05 12:04 | 45935.5026 | 2025-10-05 13:22 | 45935.5571 | 0.30222 | 0.00385 | 139 | 10911.5 | Unplanned | Vegetation | # Branch on Line, at Pole 408486, Totara North Rd, Kaeo
541 |  | INCD-34823-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-10-05 22:05 | 45935.9199 | 2025-10-06 01:42 | 45936.0708 | 5.0336 | 0.023155 | 836 | 181732.4667 | Unplanned | Third Party | # Car vs Pole, at Pole 418210, Inland Rd, Taipa
542 |  | INCD-34853-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-10-06 20:02 | 45936.8349 | 2025-10-06 21:47 | 45936.9078 | 0.10177 | 0.00096942 | 35 | 3674.4167 | Unplanned | Defective Equipment | # Repair Crossarm, at Switch 482, Waikare Rd, Kawakawa
543 |  | INCD-34862-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-10-07 08:34 | 45937.3568 | 2025-10-07 09:56 | 45937.4139 | 0.16976 | 0.0024651 | 89 | 6129.05 | Unplanned | Unknown | # Sectionaliser S1037 Tripped, Purerua Rd, Kerikeri
544 |  | INCD-34868-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-10-07 09:32 | 45937.3969 | 2025-10-07 14:43 | 45937.6132 | 1.5353 | 0.0049302 | 178 | 55429.2 | Planned | Planned Outage | # Replace Crossarms near Pole 426794, Cable Bay, Coopers Beach
545 |  | INCD-34889-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-10-30 09:31 | 45960.3965 | 2025-10-30 13:17 | 45960.5535 | 0.037558 | 0.00016619 | 6 | 1356 | Planned | Planned Outage | # Remove SWER and Clear Vegetation around Pole 417224, Broadwood
546 |  | INCD-34904-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-11-05 09:30 | 45966.3962 | 2025-11-05 13:25 | 45966.5589 | 1.4757 | 0.0063428 | 229 | 53278.2 | Planned | Planned Outage | # Replace Crossarms on Poles 421896 , 421821 , 421654 , 421665 , 421663, Oruru, Taipa
547 |  | INCD-34910-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-11-13 09:31 | 45974.3963 | 2025-11-13 12:54 | 45974.5378 | 0.32175 | 0.0015788 | 57 | 11616.6 | Planned | Planned Outage | # Maintenance on Poles 429531, Pole 429549, Pole 429548, Pole 429553, Church Rd, Kaitaia
548 |  | INCD-34913-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-10-10 22:13 | 45940.9257 | 2025-10-10 22:24 | 45940.9333 | 0.00060935 | 5.5396e-05 | 2 | 22 | Unplanned | Wildlife | # Possum Damage, Pole 440319, SH10, Waipapa
549 |  | INCD-34922-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-11-19 09:31 | 45980.3965 | 2025-11-19 13:59 | 45980.5826 | 0.03645 | 0.00013849 | 5 | 1316 | Planned | Planned Outage | # Replace SWER Poles, Hardware Beyond Link L565, Peria Valley Rd, Kaitaia
550 |  | INCD-34925-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-11-20 09:32 | 45981.3972 | 2025-11-20 11:51 | 45981.4938 | 0.01925 | 0.00013849 | 5 | 695 | Planned | Planned Outage | # Replace SWER Poles, Hardware, Beyond Links L565, Peria Valley Rd, Kaitaia
551 |  | INCD-34934-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-11-13 10:03 | 45974.4187 | 2025-11-13 15:05 | 45974.6285 | 0.10827 | 0.00038777 | 14 | 3909 | Planned | Planned Outage | # Low Lines beyond Fuse F2011, Pukakitere Rd, Omanaia
552 |  | INCD-34952-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-11-12 09:36 | 45973.4 | 2025-11-12 14:21 | 45973.5979 | 0.28451 | 0.0011633 | 42 | 10272 | Planned | Planned Outage | # Pole Replacement, Pole 430852, Whangape Rd, Kaitaia
553 |  | INCD-34961-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-10-16 20:10 | 45946.8402 | 2025-10-16 20:16 | 45946.8445 | 0.11523 | 0.018585 | 671 | 4160.2 | Unplanned | Unknown | # 33kV Church Rd to Pukenui Tripped, Pukenui South
554 |  | INCD-34964-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-10-17 11:27 | 45947.477 | 2025-10-17 11:40 | 45947.486 | 0.24113 | 0.018668 | 674 | 8705.8333 | Unplanned | Vegetation | # Shelter Belt Contact Tripped 33kV Line CHT-PKN, near Pole 201710, Turk Valley Rd, Pukenui
555 |  | INCD-34964-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-10-17 11:27 | 45947.477 | 2025-10-17 11:40 | 45947.486 | 0.20482 | 0.016951 | 612 | 7395 | Unplanned | Vegetation | # Shelter Belt Contact Tripped 33kV Line CHT-PKN, near Pole 201710, Turk Valley Rd, Pukenui
556 |  | INCD-34979-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-11-14 10:03 | 45975.4187 | 2025-11-14 13:49 | 45975.5757 | 0.26291 | 0.0011633 | 42 | 9492 | Planned | Planned Outage | # Vegetation Control, beyond L512, Otangaroa Rd, Kaeo
557 |  | INCD-34982-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-10-19 08:23 | 45949.3493 | 2025-10-19 09:32 | 45949.3972 | 0.24272 | 0.0035176 | 127 | 8763 | Unplanned | Defective Equipment | # Repair Broken Jumper at Pole 428492, West Coast Rd, Pukenui South
558 |  | INCD-34985-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-11-06 09:00 | 45967.3752 | 2025-11-06 15:20 | 45967.6389 | 4.0298 | 0.011135 | 402 | 145490.7667 | Planned | Planned Outage | # Replace Voltage Regulator Structure VR09-1, Callaghans Rd, Kawakawa
559 |  | INCD-34988-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2026-01-15 09:44 | 46037.4056 | 2026-01-15 12:53 | 46037.5368 | 0.42403 | 0.0022435 | 81 | 15309 | Planned | Planned Outage | # Replace Crossarms, at Pole 402426, Ngawha Springs Rd, Kaikohe
560 |  | INCD-34991-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2025-11-25 07:07 | 45986.2965 | 2025-11-25 17:54 | 45986.7458 | 8.737 | 0.024236 | 875 | 315442.3 | Planned | Planned Outage | # Install new Ring Main RM288, Pole 404174, Russell Rd, Haruru
561 |  | INCD-34997-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-10-20 17:41 | 45950.737 | 2025-10-20 18:42 | 45950.7795 | 1.1281 | 0.018585 | 671 | 40727.1833 | Unplanned | Unknown | # 33kV Tripped, CHT-PKN, Church Rd, Pukenui
562 |  | INCD-34997-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-10-20 17:41 | 45950.737 | 2025-10-20 18:42 | 45950.7795 | 0.31478 | 0.016757 | 605 | 11364.8167 | Unplanned | Unknown | # 33kV Tripped, CHT-PKN, Church Rd, Pukenui
563 |  | INCD-35012-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-11-20 09:01 | 45981.3758 | 2025-11-20 14:16 | 45981.5944 | 0.82933 | 0.0031852 | 115 | 29942.1667 | Planned | Planned Outage | # Upgrade Transformer T02772, Ludbrook Rd, Moerewa
564 |  | INCD-35012-F-MOEREWA | Moerewa 031322 - Moerewa |  | MOEREWA | 2025-11-20 09:01 | 45981.3758 | 2025-11-20 14:16 | 45981.5944 | 0.46585 | 0.001745 | 63 | 16819 | Planned | Planned Outage | # Upgrade Transformer T02772, Ludbrook Rd, Moerewa
565 |  | INCD-35015-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-10-23 09:35 | 45953.3993 | 2025-10-23 14:24 | 45953.6 | 1.0166 | 0.0035176 | 127 | 36703 | Planned | Planned Outage | # Vegetation Control, Beyobnd Switch 398, West Coast Rd, Kaitaia
566 |  | INCD-35024-F-PUKETONA | Haruru CB0607 - Puketona |  | PUKETONA | 2025-10-31 11:02 | 45961.4597 | 2025-10-31 13:12 | 45961.55 | 0.24485 | 0.0018834 | 68 | 8840 | Planned | Planned Outage | # Replaced HV Crossarms, Pole 4019310, Puketona Rd, Haruru
567 |  | INCD-35027-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-10-23 13:24 | 45953.5585 | 2025-10-23 14:15 | 45953.5936 | 0.11054 | 0.0021881 | 79 | 3990.8167 | Unplanned | Unknown | # Recloser R1381 Tripped, Far North Rd, Pukenui
568 |  | INCD-35033-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-12-08 09:32 | 45999.3972 | 2025-12-08 12:01 | 45999.5007 | 0.19397 | 0.0013018 | 47 | 7003 | Planned | Planned Outage | # Planned Maintenance, Beyond Switch 093, Doves Bay Rd, Waipapa
569 |  | INCD-35036-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-10-24 11:18 | 45954.4709 | 2025-10-24 12:48 | 45954.5334 | 1.6604 | 0.018585 | 671 | 59946.9167 | Unplanned | Vegetation | # Tree Contact on 33kV CHT-PKN Span, Near Pole 337735, Turk Valley Rd, Motutangi
570 |  | INCD-35036-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-10-24 11:18 | 45954.4709 | 2025-10-24 12:48 | 45954.5334 | 1.4246 | 0.016757 | 605 | 51434.8333 | Unplanned | Vegetation | # Tree Contact on 33kV CHT-PKN Span, Near Pole 337735, Turk Valley Rd, Motutangi
571 |  | INCD-35045-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-10-25 15:12 | 45955.6333 | 2025-10-25 15:18 | 45955.6375 | 0.0036561 | 0.00060935 | 22 | 132 | Unplanned | Vegetation | # Branch on Line, Near Pole 436766, SH10, Kaeo
572 |  | INCD-35057-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-12-01 09:00 | 45992.375 | 2025-12-01 13:41 | 45992.5701 | 0.26462 | 0.00094172 | 34 | 9554 | Planned | Planned Outage | # Vegetation Clearance beyond Recloser R_T01296, Pokapu Rd, Kaikohe
573 |  | INCD-35060-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-11-28 11:09 | 45989.4646 | 2025-11-28 12:17 | 45989.5118 | 0.20906 | 0.0030745 | 111 | 7548 | Planned | Planned Outage | # Remove Isolation Point L1043, SH12, Omanaia
574 |  | INCD-35069-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-10-27 12:04 | 45957.5028 | 2025-10-27 14:31 | 45957.6049 | 0.13436 | 0.00091403 | 33 | 4851 | Unplanned | Unknown | # Replace Fuses F2255, Honeymoon Valley Rd, Taipa
575 |  | INCD-35081-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-10-27 16:58 | 45957.7069 | 2025-10-28 11:51 | 45958.4938 | 0.1535 | 0.00072014 | 14 | 5542 | Unplanned | Defective Equipment | # Line Down during Storm, Near Pole 430444, Rangikohu Rd, Herekino
576 |  | INCD-35087-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-10-27 17:46 | 45957.7403 | 2025-10-27 19:49 | 45957.8257 | 0.091984 | 0.00074784 | 27 | 3321 | Unplanned | Unknown | # Sectionaliser S017 Found Open, Fern Flat Rd, Taipa
577 |  | INCD-35105-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-10-27 23:43 | 45957.9882 | 2025-10-28 02:42 | 45958.1125 | 0.20823 | 0.0011633 | 42 | 7518 | Unplanned | Adverse Weather | # Sectionaliser S004 Tripped, Unahi Rd, Kaitaia
578 |  | INCD-35108-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-10-28 05:56 | 45958.2472 | 2025-10-28 16:00 | 45958.6667 | 2.3106 | 0.018114 | 597 | 83421.3833 | Unplanned | Defective Equipment | # Line Down, Pole 406931, Onekura Rd, Waipapa
579 |  | INCD-35117-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-10-28 06:20 | 45958.2639 | 2025-10-28 17:34 | 45958.7319 | 0.13251 | 0.00085863 | 16 | 4784 | Unplanned | Defective Equipment | # Transformer T00827 Blew during Storm, Waihapa Rd, Taipa
580 |  | INCD-35123-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-10-28 05:42 | 45958.2375 | 2025-10-28 10:06 | 45958.4208 | 0.18281 | 0.00069244 | 25 | 6600 | Unplanned | Unknown | # Replace Fuse F2056, Pekerau, Taipa
581 |  | INCD-35129-F-PUKETONA | Haruru CB0607 - Puketona |  | PUKETONA | 2025-10-28 09:10 | 45958.3819 | 2025-10-28 15:16 | 45958.6361 | 0.069632 | 0.00022158 | 8 | 2514 | Unplanned | Unknown | # Fuse F2290, Blew During Storm, Puketona Rd, Haruru
582 |  | INCD-35132-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-10-28 10:57 | 45958.4562 | 2025-10-28 14:20 | 45958.5972 | 0.0051435 | 2.7698e-05 | 1 | 185.7 | Unplanned | Unknown | # Recloser R1420 Tripped during Storm, Happy Valley Rd, Kaikohe
583 |  | INCD-35132-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-10-28 10:57 | 45958.4562 | 2025-10-28 14:20 | 45958.5972 | 1.365 | 0.0078662 | 284 | 49283.6 | Unplanned | Unknown | # Recloser R1420 Tripped during Storm, Happy Valley Rd, Kaikohe
584 |  | INCD-35150-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-10-28 11:37 | 45958.4837 | 2025-10-28 13:26 | 45958.56 | 1.2798 | 0.013738 | 496 | 46205.7 | Unplanned | Unknown | # Recloser R694 Tripped, Settlers Way, Kaikohe
585 |  | INCD-35171-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-10-28 12:46 | 45958.5319 | 2025-10-29 13:09 | 45959.5479 | 0.84508 | 0.019001 | 686 | 30510.7 | Unplanned | Defective Equipment | # Blown Transformer T04144 Tripped Recloser R017, Fern Flat Rd, Taipa
586 |  | INCD-35180-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-10-28 13:32 | 45958.5642 | 2025-10-28 13:54 | 45958.5792 | 0.047008 | 0.0021881 | 79 | 1697.1833 | Unplanned | Vegetation | # Vegetation on Line, near Pole 428098, Far North Rd, Kaitaia
587 |  | INCD-35192-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-10-28 14:36 | 45958.6083 | 2025-10-28 16:11 | 45958.6743 | 0.078939 | 0.00083093 | 30 | 2850 | Unplanned | Defective Equipment | # Replace Sectionalizer S171, Wakelin Rd, Puketona
588 |  | INCD-35201-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-10-28 13:39 | 45958.5687 | 2025-10-28 17:36 | 45958.7333 | 2.2169 | 0.010968 | 396 | 80040.0667 | Unplanned | Vegetation | # Branch on Line, Pole 408385, SH10, Kaeo
589 |  | INCD-35234-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-10-28 17:50 | 45958.7431 | 2025-10-28 20:18 | 45958.8458 | 0.16804 | 0.0012741 | 43 | 6067 | Unplanned | Unknown | # SWER Line Tripped, R_T01331, Russell Rd, Kawakawa
590 |  | INCD-35237-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-10-28 16:21 | 45958.6813 | 2025-10-29 16:35 | 45959.691 | 0.42674 | 0.00055396 | 20 | 15407 | Unplanned | Defective Equipment | # Floating Conductor, due to Defective Pole 410369, Taratara Rd, Taipa
591 |  | INCD-35243-F-OMAUNU ROAD | Kaeo 191712 - Omaunu Rd |  | OMAUNU ROAD | 2025-10-28 13:30 | 45958.5625 | 2025-10-28 18:29 | 45958.7701 | 0.057971 | 0.00019388 | 7 | 2093 | Unplanned | Lightning | # Lightning Blew Fuse L603, Omanu Rd, Kaeo
592 |  | INCD-35246-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-10-28 18:13 | 45958.759 | 2025-10-29 14:15 | 45959.5938 | 0.096111 | 0.0014957 | 18 | 3470 | Unplanned | Vegetation | # Tree vs Line, near Pole 426031, Makene Rd, Mangamuka
593 |  | INCD-35249-F-SOUTH ROAD | Okahu CB1105 - South Road |  | SOUTH ROAD | 2025-10-28 15:26 | 45958.6431 | 2025-10-28 22:55 | 45958.9549 | 0.684 | 0.0015234 | 55 | 24695 | Unplanned | Defective Equipment | # Repair Conductor at Pole 407587, Larmer Rd, Kaitaia
594 |  | INCD-35255-F-MATAURI BAY | Kaeo 191732 - Matauri Bay |  | MATAURI BAY | 2025-10-29 10:55 | 45959.4548 | 2025-10-29 16:29 | 45959.6868 | 0.71903 | 0.010802 | 390 | 25959.9667 | Unplanned | Defective Equipment | # Line Down beyond Pole 435108, Matauri Bay Rd, Kaeo
595 |  | INCD-35267-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-10-30 11:44 | 45960.4889 | 2025-10-30 13:55 | 45960.5799 | 0.02177 | 0.00016619 | 6 | 786 | Unplanned | Defective Equipment | # Faulty Transformer T02066, Salvation Rd, Taipa
596 |  | INCD-35279-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-10-30 06:25 | 45960.2673 | 2025-10-30 13:01 | 45960.5421 | 0.18197 | 0.016785 | 484.2691 | 6569.8167 | Unplanned | Defective Equipment | # Broken Insulator, CHT-PKN, 33kV CB 273332
597 |  | INCD-35279-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-10-30 06:25 | 45960.2673 | 2025-10-30 13:01 | 45960.5421 | 4.0067 | 0.027476 | 792.7309 | 144658.2 | Unplanned | Defective Equipment | # Broken Insulator, CHT-PKN, 33kV CB 273332
598 |  | INCD-35285-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-10-30 15:29 | 45960.6451 | 2025-10-30 16:17 | 45960.6785 | 0.026147 | 0.00091403 | 33 | 944 | Unplanned | Unknown | # Fuse F2255 blown, Honeymoon Valley Rd, Taipa
599 |  | INCD-35291-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-11-14 09:31 | 45975.3965 | 2025-11-14 13:49 | 45975.5757 | 1.8294 | 0.0070906 | 256 | 66048 | Planned | Planned Outage | # Replace Voltage Regulator VR03-2, Far North Rd, Pukenui
600 |  | INCD-35294-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-10-31 04:00 | 45961.1665 | 2025-10-31 06:31 | 45961.2715 | 1.5234 | 0.016951 | 612 | 55000 | Unplanned | Wildlife | # Possum Across Phases, near Pole 432707, Far North Rd, Pukenui
601 |  | INCD-35312-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 0.62301 | 0.0059835 | 216.028 | 22493.0429 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
602 |  | INCD-35312-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.692 | 0.013463 | 486.0629 | 97192.3054 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
603 |  | INCD-35312-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.0862 | 0.019529 | 705.0913 | 75318.6182 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
604 |  | INCD-35312-F-POKAPU | Moerewa 031312 - Pokapu |  | POKAPU | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 1.2832 | 0.0081719 | 295.0382 | 46327.8318 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
605 |  | INCD-35312-F-ONEWHERO | Haruru CB0608 - Onewhero |  | ONEWHERO | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 0.57316 | 0.0031857 | 115.0149 | 20693.5355 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
606 |  | INCD-35312-F-TE KEMARA AVE | Haruru CB0605 - Te Kemara Ave |  | TE KEMARA AVE | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 1.9392 | 0.011081 | 400.0518 | 70011.9616 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
607 |  | INCD-35312-F-PUKETONA | Haruru CB0607 - Puketona |  | PUKETONA | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 1.2715 | 0.0070638 | 255.033 | 45907.8434 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
608 |  | INCD-35312-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.4054 | 0.023158 | 836.1083 | 86843.2706 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
609 |  | INCD-35312-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 3.1639 | 0.018615 | 672.087 | 114228.466 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
610 |  | INCD-35312-F-KAIKOHE | Kaikohe CB0107 - Kaikohe |  | KAIKOHE | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 3.4829 | 0.034654 | 1251.162 | 125746.9839 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
611 |  | INCD-35312-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 1.0577 | 0.0073963 | 267.0346 | 38187.5244 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
612 |  | INCD-35312-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 0.80799 | 0.0055403 | 200.0259 | 29171.6507 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
613 |  | INCD-35312-F-RIVERVIEW | Waipapa 041682 - Riverview |  | RIVERVIEW | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 6.7308 | 0.035098 | 1267.1641 | 243009.885 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
614 |  | INCD-35312-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 6.9626 | 0.039114 | 1412.1828 | 251378.9482 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
615 |  | INCD-35312-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 3.1774 | 0.015734 | 568.0736 | 114717.7329 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
616 |  | INCD-35312-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 4.493 | 0.025984 | 938.1215 | 162214.6478 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
617 |  | INCD-35312-F-RANUI AVENUE | Kerikeri 181172 - Ranui Ave |  | RANUI AVENUE | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.1048 | 0.015707 | 567.0734 | 75990.9831 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
618 |  | INCD-35312-F-TIMBER MILL | Mt Pokaka 171132 - Timber Mill |  | TIMBER MILL | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 0.0164 | 0.00011081 | 4.0005 | 592.1012 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
619 |  | INCD-35312-F-KARETU | Kawakawa CB0210 - Karetu |  | KARETU | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 0.91061 | 0.0053464 | 193.025 | 32876.7337 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
620 |  | INCD-35312-F-WAIPAPA BUSINESS PARK | Waipapa 041612 - Waipapa Business Park |  | WAIPAPA BUSINESS PARK | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 0.21915 | 0.0011358 | 41.0053 | 7912.3018 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
621 |  | INCD-35312-F-KAWAKAWA | Kawakawa CB0207 - Kawakawa |  | KAWAKAWA | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 1.8566 | 0.011136 | 402.0521 | 67031.5524 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
622 |  | INCD-35312-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.8122 | 0.018865 | 681.0882 | 101530.4465 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
623 |  | INCD-35312-F-KERIKERI ROAD | Kerikeri 181112 - Kerikeri Road |  | KERIKERI ROAD | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 1.5101 | 0.010942 | 395.0512 | 54519.3147 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
624 |  | INCD-35312-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.2778 | 0.013241 | 478.0619 | 82237.9337 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
625 |  | INCD-35312-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.1361 | 0.020388 | 736.0953 | 77121.4429 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
626 |  | INCD-35312-F-OMAUNU ROAD | Kaeo 191712 - Omaunu Rd |  | OMAUNU ROAD | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 0.63483 | 0.003158 | 114.0148 | 22919.8159 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
627 |  | INCD-35312-F-MOEREWA | Moerewa 031322 - Moerewa |  | MOEREWA | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.4169 | 0.01554 | 561.0726 | 87261.5587 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
628 |  | INCD-35312-F-TI BAY | Haruru CB0606 - Ti Bay |  | TI BAY | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 3.7835 | 0.021136 | 763.0988 | 136600.3382 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
629 |  | INCD-35312-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 3.1532 | 0.029779 | 1075.1392 | 113844.0336 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
630 |  | INCD-35312-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.828 | 0.03025 | 1092.1414 | 102101.2441 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
631 |  | INCD-35312-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 1.1163 | 0.012133 | 438.0567 | 40302.8858 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
632 |  | INCD-35312-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 0.91428 | 0.0045984 | 166.0215 | 33009.2063 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
633 |  | INCD-35312-F-TAU BLOCK | Moerewa 031372 - Tau Block |  | TAU BLOCK | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 0.43324 | 0.0027701 | 100.0129 | 15641.5224 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
634 |  | INCD-35312-F-NRCF | Kaikohe Transmission CB0106 - NCRF |  | NRCF | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 0.0028127 | 2.7701e-05 | 1.0001 | 101.5507 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
635 |  | INCD-35312-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 3.2815 | 0.024128 | 871.1128 | 118476.2417 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
636 |  | INCD-35312-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 1.0202 | 0.01097 | 396.0513 | 36834.2932 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
637 |  | INCD-35312-F-HONE HEKE ROAD | Kerikeri 181182 - Hone Heke Road |  | HONE HEKE ROAD | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.3193 | 0.016565 | 598.0774 | 83734.3061 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
638 |  | INCD-35312-F-AERODROME ROAD | Waipapa 041622 - Aerodrome Rd |  | AERODROME ROAD | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 1.8062 | 0.0094739 | 342.0443 | 65209.9912 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
639 |  | INCD-35312-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 5.8917 | 0.029945 | 1081.14 | 212712.142 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
640 |  | INCD-35312-F-COBHAM ROAD | Kerikeri 181132 - Cobham Road |  | COBHAM ROAD | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.254 | 0.015873 | 573.0742 | 81379.9038 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
641 |  | INCD-35312-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 3.2776 | 0.016815 | 607.0786 | 118334.6342 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
642 |  | INCD-35312-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 0.0029023 | 2.7701e-05 | 1.0001 | 104.7846 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
643 |  | INCD-35312-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 3.3554 | 0.017119 | 618.08 | 121144.5976 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
644 |  | INCD-35312-F-MATAURI BAY | Kaeo 191732 - Matauri Bay |  | MATAURI BAY | 2025-10-31 15:39 | 45961.652 | 2025-10-31 19:02 | 45961.7928 | 2.19 | 0.010804 | 390.0505 | 79066.5086 | Unplanned | Vegetation | # Southern Area Major Event, Kaikohe to Whangaroa, Far North District
645 |  | INCD-35324-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2025-11-20 09:02 | 45981.3764 | 2025-11-20 14:06 | 45981.5875 | 0.50521 | 0.0016619 | 60 | 18240 | Planned | Planned Outage | # Replace Pole 436891, Beyond Sectionaliser S164, SH10, Kaeo
646 |  | INCD-35327-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2025-11-24 09:23 | 45985.391 | 2025-11-24 14:23 | 45985.5993 | 0.13295 | 0.00044316 | 16 | 4800 | Planned | Planned Outage | # New Connection, Poles 440110 to 440118, SH10, Kaeo
647 |  | INCD-35330-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2025-11-26 09:19 | 45987.3882 | 2025-11-26 15:29 | 45987.6451 | 0.15101 | 0.00044316 | 16 | 5452 | Planned | Planned Outage | # Upgrade Transformer T02966, SH10, Kaeo
648 |  | INCD-35336-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-11-03 08:09 | 45964.3393 | 2025-11-03 08:38 | 45964.3597 | 0.16279 | 0.015732 | 568 | 5877.3 | Unplanned | Defective Equipment | # Line Down, near Pole 207807, Hospital Rd, Kaeo
649 |  | INCD-35342-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-11-26 09:32 | 45987.3972 | 2025-11-26 16:06 | 45987.6708 | 0.42123 | 0.0011079 | 40 | 15208 | Planned | Planned Outage | # Replace Transformer Pole 418927, Taylor Rd, Taipa
650 |  | INCD-35348-F-TI BAY | Haruru CB0606 - Ti Bay |  | TI BAY | 2025-11-27 09:46 | 45988.4071 | 2025-11-27 14:01 | 45988.5843 | 3.1368 | 0.012298 | 444 | 113249.6 | Planned | Planned Outage | # Install New Conductors near Poles 405309, Puketona Rd, Haruru
651 |  | INCD-35351-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-11-04 11:46 | 45965.4901 | 2025-11-04 13:22 | 45965.5569 | 0.19438 | 0.0020219 | 73 | 7017.7333 | Unplanned | Defective Equipment | # Broken Lead, at Pole 415165, West Coast Rd, Mitimiti
652 |  | INCD-35375-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-11-26 10:05 | 45987.4201 | 2025-11-26 13:11 | 45987.5493 | 0.16486 | 0.00088633 | 32 | 5952 | Planned | Planned Outage | # Replaced Pole 433665, SH12, Omanaia
653 |  | INCD-35378-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-11-17 09:29 | 45978.3951 | 2025-11-17 11:57 | 45978.4979 | 0.0040993 | 2.7698e-05 | 1 | 148 | Planned | Planned Outage | # Vegetation Control, Near Transformer T00387, Waikare Rd, Kawakawa
654 |  | INCD-35384-F-AERODROME ROAD | Waipapa 041622 - Aerodrome Rd |  | AERODROME ROAD | 2025-11-04 23:40 | 45965.9861 | 2025-11-05 13:49 | 45966.5757 | 2.3296 | 0.0050133 | 181 | 84108 | Unplanned | Third Party | # Car vs Pole vs Transformer, T08998, Puketotara Rd, Waipapa
655 |  | INCD-35387-F-POKAPU | Moerewa 031312 - Pokapu |  | POKAPU | 2025-11-05 14:12 | 45966.5916 | 2025-11-05 14:34 | 45966.6072 | 0.091814 | 0.0040716 | 147 | 3314.85 | Unplanned | Unknown | # Recloser R481 Tripped, Otiria Rd, Moerewa
656 |  | INCD-35390-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-11-05 15:05 | 45966.6285 | 2025-11-05 17:20 | 45966.7222 | 0.0037392 | 2.7698e-05 | 1 | 135 | Unplanned | Defective Equipment | # Restrain Low HV Conductor, near Pole 412703, Mata Rd, Kaikohe
657 |  | INCD-35390-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-11-05 15:05 | 45966.6285 | 2025-11-05 17:20 | 45966.7222 | 0.20192 | 0.0014957 | 54 | 7290 | Unplanned | Defective Equipment | # Restrain Low HV Conductor, near Pole 412703, Mata Rd, Kaikohe
658 |  | INCD-35417-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 1.5171 | 0.0059835 | 209.9972 | 54774.9041 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
659 |  | INCD-35417-F-POKAPU | Moerewa 031312 - Pokapu |  | POKAPU | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 2.3424 | 0.0081719 | 286.8018 | 84569.3456 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
660 |  | INCD-35417-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 7.5423 | 0.022992 | 806.9338 | 272307.9553 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
661 |  | INCD-35417-F-KAIKOHE | Kaikohe CB0107 - Kaikohe |  | KAIKOHE | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 8.5459 | 0.034654 | 1216.2339 | 308542.2495 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
662 |  | INCD-35417-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 8.0818 | 0.025984 | 911.9324 | 291786.9205 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
663 |  | INCD-35417-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 3.5717 | 0.021884 | 768.0454 | 128953.6623 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
664 |  | INCD-35417-F-KAWAKAWA | Kawakawa CB0207 - Kawakawa |  | KAWAKAWA | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 3.3009 | 0.011136 | 390.8282 | 119177.1325 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
665 |  | INCD-35417-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 5.0917 | 0.019529 | 685.4076 | 183832.4484 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
666 |  | INCD-35417-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 1.9412 | 0.015734 | 552.2149 | 70085.836 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
667 |  | INCD-35417-F-RANUI AVENUE | Kerikeri 181172 - Ranui Ave |  | RANUI AVENUE | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 4.7121 | 0.015707 | 551.2427 | 170125.1704 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
668 |  | INCD-35417-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 5.5822 | 0.018615 | 653.3247 | 201540.3184 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
669 |  | INCD-35417-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 1.9059 | 0.0055403 | 194.4419 | 68810.1806 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
670 |  | INCD-35417-F-TE KEMARA AVE | Haruru CB0605 - Te Kemara Ave |  | TE KEMARA AVE | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 3.8229 | 0.011081 | 388.8838 | 138020.4204 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
671 |  | INCD-35417-F-KARETU | Kawakawa CB0210 - Karetu |  | KARETU | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 1.6364 | 0.0053463 | 187.6364 | 59079.6076 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
672 |  | INCD-35417-F-TIMBER MILL | Mt Pokaka 171132 - Timber Mill |  | TIMBER MILL | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 0.03701 | 0.00011081 | 3.8888 | 1336.1977 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
673 |  | INCD-35417-F-PUKETONA | Haruru CB0607 - Puketona |  | PUKETONA | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 2.4724 | 0.0070638 | 247.9134 | 89263.2067 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
674 |  | INCD-35417-F-WAIPAPA BUSINESS PARK | Waipapa 041612 - Waipapa Business Park |  | WAIPAPA BUSINESS PARK | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 0.40975 | 0.0011358 | 39.8606 | 14793.6221 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
675 |  | INCD-35417-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 13.4947 | 0.039114 | 1372.7596 | 487212.0841 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
676 |  | INCD-35417-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 5.0689 | 0.013463 | 472.4938 | 183006.0762 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
677 |  | INCD-35417-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 6.0006 | 0.023158 | 812.767 | 216644.353 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
678 |  | INCD-35417-F-TAU BLOCK | Moerewa 031372 - Tau Block |  | TAU BLOCK | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 0.79811 | 0.0027701 | 97.2209 | 28814.9632 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
679 |  | INCD-35417-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 8.1085 | 0.029779 | 1045.1251 | 292747.8961 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
680 |  | INCD-35417-F-ONEWHERO | Haruru CB0608 - Onewhero |  | ONEWHERO | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 1.1025 | 0.0031856 | 111.8041 | 39805.8894 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
681 |  | INCD-35417-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 5.4611 | 0.020388 | 715.5461 | 197166.7713 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
682 |  | INCD-35417-F-MOEREWA | Moerewa 031322 - Moerewa |  | MOEREWA | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 4.4052 | 0.01543 | 541.5206 | 159047.0314 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
683 |  | INCD-35417-F-HONE HEKE ROAD | Kerikeri 181182 - Hone Heke Road |  | HONE HEKE ROAD | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 5.6489 | 0.016565 | 581.3812 | 203948.1746 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
684 |  | INCD-35417-F-KERIKERI ROAD | Kerikeri 181112 - Kerikeri Road |  | KERIKERI ROAD | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 3.7313 | 0.010942 | 384.0227 | 134714.9314 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
685 |  | INCD-35417-F-TI BAY | Haruru CB0606 - Ti Bay |  | TI BAY | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 7.3344 | 0.021136 | 741.7958 | 264800.1778 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
686 |  | INCD-35417-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 3.4886 | 0.012133 | 425.8277 | 125950.9347 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
687 |  | INCD-35417-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 1.7226 | 0.0045984 | 161.3868 | 62192.8016 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
688 |  | INCD-35417-F-MATAURI BAY | Kaeo 191732 - Matauri Bay |  | MATAURI BAY | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 4.0359 | 0.010803 | 379.1617 | 145712.5585 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
689 |  | INCD-35417-F-NRCF | Kaikohe Transmission CB0106 - NCRF |  | NRCF | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 0.006955 | 2.7701e-05 | 0.97221 | 251.1038 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
690 |  | INCD-35417-F-RIVERVIEW | Waipapa 041682 - Riverview |  | RIVERVIEW | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 12.6436 | 0.035097 | 1231.7893 | 456483.1711 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
691 |  | INCD-35417-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 10.848 | 0.037729 | 1324.1492 | 391655.2963 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
692 |  | INCD-35417-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 6.4235 | 0.018837 | 661.1024 | 231914.3123 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
693 |  | INCD-35417-F-OMAUNU ROAD | Kaeo 191712 - Omaunu Rd |  | OMAUNU ROAD | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 1.1907 | 0.0031579 | 110.8319 | 42990.0605 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
694 |  | INCD-35417-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 11.0624 | 0.029945 | 1050.9583 | 399395.8415 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
695 |  | INCD-35417-F-COBHAM ROAD | Kerikeri 181132 - Cobham Road |  | COBHAM ROAD | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 4.5397 | 0.015873 | 557.076 | 163902.2497 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
696 |  | INCD-35417-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 6.2135 | 0.017119 | 600.8254 | 224333.8907 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
697 |  | INCD-35417-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 2.5394 | 0.0073962 | 259.5799 | 91683.5648 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
698 |  | INCD-35417-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 0.0074199 | 2.7701e-05 | 0.97221 | 267.8896 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
699 |  | INCD-35417-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 4.0249 | 0.013241 | 464.7161 | 145315.7998 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
700 |  | INCD-35417-F-AERODROME ROAD | Waipapa 041622 - Aerodrome Rd |  | AERODROME ROAD | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 3.4233 | 0.0094738 | 332.4956 | 123595.1362 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
701 |  | INCD-35417-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-11-06 17:21 | 45967.7232 | 2025-11-06 23:44 | 45967.9889 | 6.3143 | 0.016815 | 590.1311 | 227972.3457 | Unplanned | Defective Equipment | # Southern Area Network Outage, Kaikohe Substation, 33kV Bus
702 |  | INCD-35426-F-KARETU | Kawakawa CB0210 - Karetu |  | KARETU | 2025-11-08 11:12 | 45969.4667 | 2025-11-08 12:31 | 45969.5215 | 0.096277 | 0.0012187 | 44 | 3476 | Unplanned | Defective Equipment | # Replaced Crossarm on Pole 403146, Settlement Rd, Kawakawa
703 |  | INCD-35432-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-11-08 16:15 | 45969.6768 | 2025-11-08 21:56 | 45969.9139 | 3.4296 | 0.012132 | 438 | 123822.6 | Unplanned | Vegetation | # Vegetation on Line, near Pole 327954, Tripped Generator to Substation, Jordan Rd, Taheke
704 |  | INCD-35432-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-11-08 16:15 | 45969.6768 | 2025-11-08 21:56 | 45969.9139 | 9.6565 | 0.030274 | 1093 | 348637.1833 | Unplanned | Vegetation | # Vegetation on Line, near Pole 327954, Tripped Generator to Substation, Jordan Rd, Taheke
705 |  | INCD-35432-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2025-11-08 16:15 | 45969.6768 | 2025-11-08 21:56 | 45969.9139 | 1.654 | 0.0059827 | 216 | 59715.2333 | Unplanned | Vegetation | # Vegetation on Line, near Pole 327954, Tripped Generator to Substation, Jordan Rd, Taheke
706 |  | INCD-35432-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-11-08 16:15 | 45969.6768 | 2025-11-08 21:56 | 45969.9139 | 3.3846 | 0.010968 | 396 | 122199.0333 | Unplanned | Vegetation | # Vegetation on Line, near Pole 327954, Tripped Generator to Substation, Jordan Rd, Taheke
707 |  | INCD-35438-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-11-08 20:14 | 45969.8429 | 2025-11-08 21:07 | 45969.8802 | 0.28327 | 0.0055396 | 200 | 10227 | Unplanned | Vegetation | # Branch on Line at Pole 440752, Wakelin Rd, Bull's Gorge
708 |  | INCD-35441-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-11-08 20:49 | 45969.8672 | 2025-11-08 21:07 | 45969.8799 | 0.16247 | 0.010248 | 200 | 5865.8333 | Unplanned | Vegetation | # Tree on Line, near Pole 440752, Wakelin Rd, Bull's Gorge
709 |  | INCD-35450-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-11-08 23:21 | 45969.9732 | 2025-11-09 03:27 | 45970.1438 | 1.6753 | 0.0069798 | 252 | 60486.7167 | Unplanned | Vegetation | # Branch on Line, near 423742, Towai Rd, Kawakawa
710 |  | INCD-35456-F-MATAURI BAY | Kaeo 191732 - Matauri Bay |  | MATAURI BAY | 2025-11-27 11:06 | 45988.4625 | 2025-11-27 13:05 | 45988.5451 | 0.046144 | 0.00038777 | 14 | 1666 | Planned | Planned Outage | # Install Pole 338822, Martin Rd, Kaeo
711 |  | INCD-35465-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-11-27 09:39 | 45988.4021 | 2025-11-27 12:50 | 45988.5347 | 0.2169 | 0.0011356 | 41 | 7831 | Planned | Planned Outage | # Replace Poles near T00157, Taylor Rd, Taipa
712 |  | INCD-35468-F-POKAPU | Moerewa 031312 - Pokapu |  | POKAPU | 2025-11-20 10:35 | 45981.441 | 2025-11-20 11:49 | 45981.4924 | 0.067638 | 0.00091403 | 33 | 2442 | Planned | Planned Outage | # Replace Crossarm, at Pole 4019752, Pokapu Rd, Moerewa
713 |  | INCD-35471-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-11-12 14:29 | 45973.6032 | 2025-11-12 15:14 | 45973.6347 | 0.78997 | 0.019555 | 706 | 28520.9167 | Unplanned | Unknown | # Recloser R587 Tripped, Te Pua Rd, Kaikohe
714 |  | INCD-35471-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-11-12 14:29 | 45973.6032 | 2025-11-12 15:14 | 45973.6347 | 0.001257 | 2.7698e-05 | 1 | 45.3833 | Unplanned | Unknown | # Recloser R587 Tripped, Te Pua Rd, Kaikohe
715 |  | INCD-35474-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-11-12 14:38 | 45973.6097 | 2025-11-12 15:13 | 45973.634 | 0.043624 | 0.0012464 | 45 | 1575 | Unplanned | Third Party | # Digger brought LV Line Down, Tripping Recloser R_T01298, West Coast Rd, Kaitaia
716 |  | INCD-35477-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-11-12 15:20 | 45973.6389 | 2025-11-12 20:51 | 45973.8685 | 3.0975 | 0.0096111 | 347 | 111833.1833 | Unplanned | Vegetation | # Lines Down, near Pole 416312, Mangakahia Rd, Kaikohe
717 |  | INCD-35480-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-11-12 16:24 | 45973.6835 | 2025-11-12 18:37 | 45973.7757 | 0.0018465 | 2.7698e-05 | 1 | 66.6667 | Unplanned | Unknown | # Recloser R587 Tripped, Second Time, Te Pua Rd, Kaikohe
718 |  | INCD-35480-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-11-12 16:24 | 45973.6835 | 2025-11-12 18:37 | 45973.7757 | 1.4571 | 0.019555 | 706 | 52605.9333 | Unplanned | Unknown | # Recloser R587 Tripped, Second Time, Te Pua Rd, Kaikohe
719 |  | INCD-35489-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-12-03 09:11 | 45994.3826 | 2025-12-03 14:08 | 45994.5889 | 0.47712 | 0.0016065 | 58 | 17226 | Planned | Planned Outage | # Replace Poles from 417971 to 417977, Taronui Rd, Waipapa
720 |  | INCD-35501-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2025-11-13 17:35 | 45974.7326 | 2025-11-13 22:49 | 45974.9507 | 0.36184 | 0.001191 | 43 | 13064 | Unplanned | Unknown | # Broken Line between Transformers T05187 and T08708, Waikare Rd, Kawakawa
721 |  | INCD-35516-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-11-15 05:20 | 45976.2221 | 2025-11-15 07:06 | 45976.2959 | 0.0029447 | 2.7698e-05 | 1 | 106.3167 | Unplanned | Unknown | # Sectionaliser S1065 Tripped Off, Hobson Rd, Kaikohe
722 |  | INCD-35516-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-11-15 05:20 | 45976.2221 | 2025-11-15 07:06 | 45976.2959 | 0.22674 | 0.0021327 | 77 | 8186.3833 | Unplanned | Unknown | # Sectionaliser S1065 Tripped Off, Hobson Rd, Kaikohe
723 |  | INCD-35528-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-11-15 16:12 | 45976.675 | 2025-11-15 17:02 | 45976.7094 | 0.076651 | 0.0055396 | 200 | 2767.4 | Unplanned | Defective Equipment | # Repaired Flipped Crossarm, at Pole 432350, Far North Rd, Pukenui
724 |  | INCD-35531-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-11-15 15:15 | 45976.6354 | 2025-11-15 17:34 | 45976.7319 | 0.00385 | 2.7698e-05 | 1 | 139 | Unplanned | Unknown | # Blown Fuse, L588, Te Tio Rd, Kaikohe
725 |  | INCD-35534-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-12-09 09:33 | 46000.3981 | 2025-12-09 10:38 | 46000.4431 | 1.2505 | 0.020275 | 732 | 45146.3 | Planned | Planned Outage | # Planned work on New Broadwood Feeder, Ruaroa Rd, Kaitaia
726 |  | INCD-35537-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-12-12 09:11 | 46003.3826 | 2025-12-12 13:50 | 46003.5764 | 0.45593 | 0.0016342 | 59 | 16461 | Planned | Planned Outage | # Replace Crossarms, near Pole 417916, Te Tii Rd, Waipapa
727 |  | INCD-35546-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-11-17 12:09 | 45978.5062 | 2025-11-17 13:45 | 45978.5729 | 0.093064 | 0.00096942 | 35 | 3360 | Unplanned | Unknown | # Repair Broken Jumper, at Transformer T08747, West Coast Rd, Mitimiti
728 |  | INCD-35549-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-11-23 11:08 | 45984.4639 | 2025-11-23 13:27 | 45984.5604 | 1.8133 | 0.013046 | 471 | 65469 | Planned | Planned Outage | # Replace Poles and Crossarms, near Transformer T03749, SH1, Okaihau
729 |  | INCD-35549-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-11-23 11:08 | 45984.4639 | 2025-11-23 13:27 | 45984.5604 | 0.00385 | 2.7698e-05 | 1 | 139 | Planned | Planned Outage | # Replace Poles and Crossarms, near Transformer T03749, SH1, Okaihau
730 |  | INCD-35588-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-11-18 14:33 | 45979.6062 | 2025-11-18 17:36 | 45979.733 | 2.5861 | 0.019555 | 706 | 93366.8333 | Unplanned | Defective Equipment | # Replace Insulators at Pole 336755, SH1, Kaikohe
731 |  | INCD-35588-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-11-18 14:33 | 45979.6062 | 2025-11-18 17:36 | 45979.733 | 0.0050595 | 2.7698e-05 | 1 | 182.6667 | Unplanned | Defective Equipment | # Replace Insulators at Pole 336755, SH1, Kaikohe
732 |  | INCD-35591-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-11-18 14:33 | 45979.6062 | 2025-11-18 15:05 | 45979.6285 | 0.032794 | 0.0010248 | 37 | 1184 | Unplanned | Defective Equipment | # Repair Crossarm, at Pole 427294, Roma Rd, Ahipara
733 |  | INCD-35594-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-11-18 16:15 | 45979.6773 | 2025-11-18 19:37 | 45979.8176 | 1.1187 | 0.0055396 | 200 | 40389 | Unplanned | Third Party | # Digger vs Line, near Pole 440704, Wakelin Rd, Puketona
734 |  | INCD-35597-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-11-18 16:45 | 45979.6978 | 2025-11-18 18:33 | 45979.7729 | 0.26372 | 0.0026036 | 94 | 9521.2333 | Unplanned | Vegetation | # Branch on Line, at Pole 416771, Rangihoua Rd, Waipapa
735 |  | INCD-35606-F-VICTORIA VALLEY | Kaitaia Transmission 151802 - Victoria Valley |  | VICTORIA VALLEY | 2025-12-04 09:42 | 45995.4042 | 2025-12-04 14:23 | 45995.5993 | 0.38137 | 0.0013572 | 49 | 13769 | Planned | Planned Outage | # Replace Pole 428923, SH1, Kaitaia
736 |  | INCD-35621-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-11-20 11:17 | 45981.4701 | 2025-11-20 13:38 | 45981.5681 | 0.070297 | 0.00049856 | 18 | 2538 | Unplanned | Vegetation | # Tree in Conductor Span, Pole 418828, Fairburn Rd, Kaitaia
737 |  | INCD-35630-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2025-11-27 09:34 | 45988.3986 | 2025-11-27 14:32 | 45988.6056 | 1.2572 | 0.0043485 | 157 | 45391 | Planned | Planned Outage | # Crossarm Replacement, Multiple Sites, SH12, Waima
738 |  | INCD-35645-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-12-09 09:39 | 46000.4021 | 2025-12-09 12:14 | 46000.5097 | 0.10304 | 0.00066475 | 24 | 3720 | Planned | Planned Outage | # Reconductoring, Beyond Fuse F2032, Peria Valley Rd, Kaitaia
739 |  | INCD-35648-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-12-09 09:44 | 46000.4056 | 2025-12-09 13:04 | 46000.5444 | 0.7977 | 0.0039885 | 144 | 28800 | Planned | Planned Outage | # Replace Crossarms, near Switch 669, Waipapa West Rd, Waipapa
740 |  | INCD-35651-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2025-12-10 08:34 | 46001.3569 | 2025-12-10 13:27 | 46001.5604 | 0.040577 | 0.00013849 | 5 | 1465 | Planned | Planned Outage | # Vegetation Clearance, Beyond Switch 690, Puketona Rd, Haruru
741 |  | INCD-35654-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-12-10 09:39 | 46001.4021 | 2025-12-10 13:51 | 46001.5771 | 0.18774 | 0.00074784 | 27 | 6778 | Planned | Planned Outage | # Install Isolation Points, Beyond Switch 064, Fern Flat Rd, Taipa
742 |  | INCD-35660-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-11-22 18:31 | 45983.7715 | 2025-11-22 20:15 | 45983.8438 | 0.0086417 | 8.3093e-05 | 3 | 312 | Unplanned | Unknown | # Fuse L769 Blown, Taupo Bay Road, Taipa
743 |  | INCD-35669-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-12-11 09:06 | 46002.3792 | 2025-12-11 14:21 | 46002.5979 | 0.92483 | 0.002936 | 106 | 33390 | Planned | Planned Outage | # Planned Pole and Switch Replacement beyond Switch 761, Tauranga Rd, Kaeo
744 |  | INCD-35675-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-12-11 09:32 | 46002.3972 | 2025-12-11 14:21 | 46002.5979 | 1.665 | 0.0057611 | 208 | 60112 | Planned | Planned Outage | # Replace Pole and Isolation Point, Pole 428297, Far North Rd, Kaitaia
745 |  | INCD-35681-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2025-12-15 09:27 | 46006.3938 | 2025-12-18 15:04 | 46009.6278 | 0.14206 | 0.00024928 | 9 | 5129 | Planned | Planned Outage | # Remove Conductors Between Poles 400802 and 912352 for Tree Cutting, Riddell Rd, Kerikeri
746 |  | INCD-35684-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2025-12-18 13:03 | 46009.5437 | 2025-12-18 15:04 | 46009.6278 | 0.026811 | 0.00022158 | 8 | 968 | Planned | Planned Outage | # Reinstate Span between Poles 400802 and 912352, Riddell Rd, Kerikeri
747 |  | INCD-35696-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-11-24 12:17 | 45985.5119 | 2025-11-25 09:08 | 45986.3807 | 2.0932 | 0.037799 | 1311.9695 | 75572.2812 | Unplanned | Unknown | # 33kV Circuit Breaker 151162 Tripped, Kaitaia to Taipa
748 |  | INCD-35696-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-11-24 12:17 | 45985.5119 | 2025-11-25 09:08 | 45986.3807 | 2.63 | 0.044871 | 1557.4223 | 94954.5597 | Unplanned | Unknown | # 33kV Circuit Breaker 151162 Tripped, Kaitaia to Taipa
749 |  | INCD-35696-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-11-24 12:17 | 45985.5119 | 2025-11-25 09:08 | 45986.3807 | 2.0414 | 0.049919 | 1732.6082 | 73702.8258 | Unplanned | Unknown | # 33kV Circuit Breaker 151162 Tripped, Kaitaia to Taipa
750 |  | INCD-35705-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-12-05 09:33 | 45996.3979 | 2025-12-05 12:28 | 45996.5194 | 0.092095 | 0.00052626 | 19 | 3325 | Planned | Planned Outage | # Replace Pole 428012, Paparore Rd, Pukenui
751 |  | INCD-35729-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2025-12-10 10:00 | 46001.4168 | 2025-12-10 14:46 | 46001.6153 | 0.4195 | 0.001468 | 53 | 15145.6333 | Planned | Planned Outage | # Install Sectionaliser S1334, SH1, Kaitaia
752 |  | INCD-35729-F-SOUTH ROAD | Okahu CB1105 - South Road |  | SOUTH ROAD | 2025-12-10 10:00 | 46001.4168 | 2025-12-10 14:46 | 46001.6153 | 0.50364 | 0.0017727 | 64 | 18183.4667 | Planned | Planned Outage | # Install Sectionaliser S1334, SH1, Kaitaia
753 |  | INCD-35732-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-12-15 09:19 | 46006.3882 | 2025-12-15 12:52 | 46006.5361 | 1.0581 | 0.0092788 | 335 | 38201 | Planned | Planned Outage | # Isolation Work at Transformer T0297, Takahe Rd, Kaitaia
754 |  | INCD-35735-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-11-26 19:18 | 45987.8042 | 2025-11-26 22:37 | 45987.9424 | 0.010996 | 5.5396e-05 | 2 | 397 | Unplanned | Defective Equipment | # Repaired Loose Joint, at Pole 214046, Sandhills Rd, Awanui
755 |  | INCD-35747-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-11-28 02:00 | 45989.0836 | 2025-11-28 03:42 | 45989.1541 | 1.1311 | 0.011135 | 402 | 40836.5 | Planned | Planned Outage | # Remove Temporary Links TL818, near Switch 1327M, Wrathall Rd, Taipa
756 |  | INCD-35750-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-11-28 09:38 | 45989.4014 | 2025-11-28 11:49 | 45989.4924 | 0.025399 | 0.00019388 | 7 | 917 | Unplanned | Defective Equipment | # Line Joint Failed, Pole 407487, Waiotehue Rd, Kaitaia
757 |  | INCD-35759-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-11-29 00:19 | 45990.013 | 2025-11-29 00:39 | 45990.0273 | 0.31332 | 0.016785 | 606 | 11312 | Unplanned | Lightning | # Lightning Strike Tripped off Pukenui Substation, 119 Lamb Road, Pukenui
758 |  | INCD-35759-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-11-29 00:19 | 45990.013 | 2025-11-29 00:39 | 45990.0273 | 0.38591 | 0.018613 | 672 | 13932.8 | Unplanned | Lightning | # Lightning Strike Tripped off Pukenui Substation, 119 Lamb Road, Pukenui
759 |  | INCD-35762-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-11-28 22:49 | 45989.9507 | 2025-11-29 01:36 | 45990.0667 | 0.027753 | 0.00016619 | 6 | 1002 | Unplanned | Lightning | # Replaced Fuse F2138, Opara Rd, Omanaia
760 |  | INCD-35777-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-12-12 09:34 | 46003.3986 | 2025-12-12 13:04 | 46003.5444 | 0.73496 | 0.0037669 | 136 | 26535 | Planned | Planned Outage | # Install Drop Out Fuse Holders, at Transformer T04497, Kaitaia-Awaroa Rd, Kaitaia
761 |  | INCD-35780-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2025-12-17 09:04 | 46008.3778 | 2025-12-17 13:48 | 46008.575 | 0.73942 | 0.0026036 | 94 | 26696 | Planned | Planned Outage | # Planned Replacement of Poles 437275 to 437288, Tauranga Bay Rd, Whangaroa
762 |  | INCD-35783-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-12-17 09:11 | 46008.3826 | 2025-12-17 13:18 | 46008.5542 | 0.23261 | 0.00094172 | 34 | 8398 | Planned | Planned Outage | # Vegetation Clearance, Beyond Switch 793, Kimberley Rd, Pukenui
763 |  | INCD-35789-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-01-08 09:33 | 46030.3979 | 2026-01-08 11:55 | 46030.4965 | 0.38938 | 0.0027421 | 99 | 14058 | Planned | Planned Outage | # Replace Crossarm on Pole 417648, Pawarenga Rd, Kaitaia
764 |  | INCD-35792-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2026-01-08 09:33 | 46030.398 | 2026-01-08 14:53 | 46030.6201 | 1.8474 | 0.0069798 | 252 | 66698.0333 | Planned | Planned Outage | # Network Alternations, Beyond Recloser R131, Towai Rd, Kawakawa
765 |  | INCD-35798-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-12-01 13:42 | 45992.571 | 2025-12-01 14:03 | 45992.5854 | 0.026839 | 0.0013018 | 47 | 968.9833 | Unplanned | Unknown | # Sectionaliser S1057 Tripped, Waihotu Rd, Omanaia
766 |  | INCD-35801-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-12-18 09:28 | 46009.3944 | 2025-12-18 14:38 | 46009.6097 | 0.20807 | 0.00072014 | 26 | 7512 | Planned | Planned Outage | # Resag Conductor between Poles 438714 - 438731, SH12, Omanaia
767 |  | INCD-35804-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2025-12-01 14:50 | 45992.6183 | 2025-12-01 15:34 | 45992.6484 | 0.32031 | 0.016785 | 606 | 11564.3667 | Unplanned | Other Cause | # Fire Under Lines, near Transformer T09204, Far North Rd, Pukenui
768 |  | INCD-35807-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2025-12-01 14:13 | 45992.5923 | 2025-12-01 15:04 | 45992.628 | 0.066977 | 0.0013018 | 47 | 2418.15 | Unplanned | Vegetation | # Branch on Line, near Pole 450964, Wharekawa Rd, Omanaia
769 |  | INCD-35810-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2025-12-11 09:42 | 46002.4042 | 2025-12-11 11:31 | 46002.4799 | 0.019056 | 0.00060935 | 22 | 688 | Planned | Planned Outage | # Planned Vegetation Control, near Pole 423271, Hay Rd, Kawakawa
770 |  | INCD-35819-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-12-02 11:03 | 45993.4601 | 2025-12-02 12:52 | 45993.5361 | 0.1122 | 0.0010248 | 37 | 4050.8833 | Planned | Planned Outage | # New Feeder 151822 Clough Rd, Kaitaia Substation Brought on Line, SH1, Kaitaia
771 |  | INCD-35831-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2025-12-16 09:03 | 46007.3771 | 2025-12-16 14:31 | 46007.6049 | 0.67023 | 0.0021604 | 78 | 24198 | Planned | Planned Outage | # Reconfigure Network near Link L411, Kapiro Rd, Waipapa
772 |  | INCD-35834-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-12-16 09:38 | 46007.4012 | 2025-12-16 15:07 | 46007.6302 | 2.5918 | 0.0078662 | 284 | 93574.3333 | Planned | Planned Outage | # Replace Sectionalisers with Autolinks, Beyond Switch 324, Kaitaia Awaroa Rd, Kaitaia
773 |  | INCD-35837-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2025-12-03 06:51 | 45994.2857 | 2025-12-03 06:56 | 45994.2891 | 0.037724 | 0.018862 | 681 | 1362 | Unplanned | Human Error | # Onsite Switching Tripped Substation, SH10, Mt Pokaka
774 |  | INCD-35837-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-12-03 06:51 | 45994.2857 | 2025-12-03 06:56 | 45994.2891 | 0.027698 | 0.0055396 | 200 | 1000 | Unplanned | Human Error | # Onsite Switching Tripped Substation, SH10, Mt Pokaka
775 |  | INCD-35837-F-TIMBER MILL | Mt Pokaka 171132 - Timber Mill |  | TIMBER MILL | 2025-12-03 06:51 | 45994.2857 | 2025-12-03 06:56 | 45994.2891 | 0.00011079 | 0.00011079 | 4 | 4 | Unplanned | Human Error | # Onsite Switching Tripped Substation, SH10, Mt Pokaka
776 |  | INCD-35840-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-12-03 09:01 | 45994.3758 | 2025-12-03 14:54 | 45994.6206 | 2.0293 | 0.046089 | 837 | 73267.65 | Planned | Planned Outage | # Maintanance and New Connections, at Pole 418099, Inland Rd, Taipa
777 |  | INCD-35843-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-12-03 10:28 | 45994.4361 | 2025-12-03 15:09 | 45994.6312 | 0.077831 | 0.00027698 | 10 | 2810 | Planned | Planned Outage | # Planned Shutdown beyond Fuse F2252, Inland Rd, Karikari
778 |  | INCD-35861-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-12-03 16:41 | 45994.6954 | 2025-12-03 18:50 | 45994.7847 | 0.25756 | 0.0055396 | 200 | 9299 | Unplanned | Defective Equipment | # Line Down at Pole 440703, Wakelin Rd, Puketona
779 |  | INCD-35864-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-12-03 16:39 | 45994.6937 | 2025-12-03 21:22 | 45994.8903 | 0.046006 | 0.00047086 | 17 | 1661 | Unplanned | Defective Equipment | # Lead Off Top of Fuse F_T02911, Picadilly Rd, Kaikohe
780 |  | INCD-35882-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2025-12-04 00:35 | 45995.0244 | 2025-12-04 02:23 | 45995.0993 | 3.0674 | 0.030301 | 1094 | 110746.55 | Unplanned | Vegetation | # Branch on Line, at Pole 214540, SH12, Omanaia
781 |  | INCD-35888-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-12-04 06:00 | 45995.2498 | 2025-12-04 10:03 | 45995.4187 | 0.65696 | 0.0054842 | 198 | 23718.8667 | Unplanned | Defective Equipment | # Line Down at Pole 409298, Mangakaretu Rd, Waipapa
782 |  | INCD-35900-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2025-12-04 06:10 | 45995.2569 | 2025-12-04 09:48 | 45995.4083 | 0.14491 | 0.00066475 | 24 | 5232 | Unplanned | Unknown | # Fuse F2063 Blown, Te Ahu Rd, Pukenui
783 |  | INCD-35903-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-12-04 09:31 | 45995.3965 | 2025-12-04 13:11 | 45995.5491 | 1.808 | 0.0082262 | 297 | 65275.65 | Planned | Planned Outage | # Service Transformer T03716, Horeke Rd, Kaikohe
784 |  | INCD-35906-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-12-04 09:39 | 45995.4021 | 2025-12-04 15:17 | 45995.6368 | 0.61356 | 0.0027698 | 100 | 22152 | Planned | Planned Outage | # Outage for Close Approach, Horeke Rd, Kaikohe
785 |  | INCD-35912-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-12-04 09:15 | 45995.3854 | 2025-12-04 13:19 | 45995.555 | 0.22725 | 0.0021327 | 77 | 8204.5667 | Unplanned | Defective Equipment | # Repair Switch 042, Puketotara Rd, Waipapa
786 |  | INCD-35918-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-12-04 15:12 | 45995.6333 | 2025-12-04 19:11 | 45995.7993 | 1.778 | 0.0084201 | 304 | 64193 | Unplanned | Vegetation | # Tree Thorugh Line at Pole 431276, Te Ahu Ahu Rd, Kaikohe
787 |  | INCD-35933-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-01-06 09:33 | 46028.3979 | 2026-01-06 11:24 | 46028.475 | 0.052266 | 0.00047086 | 17 | 1887 | Planned | Planned Outage | # Network Alterations, Beyond Switch 334, Oruaiti Rd, Taipa
788 |  | INCD-35936-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-01-14 09:34 | 46036.3986 | 2026-01-14 13:22 | 46036.5569 | 0.25892 | 0.0011356 | 41 | 9348 | Planned | Planned Outage | # Network Alterations, Beyond Link L569, Taylor Rd, Taipa
789 |  | INCD-35939-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2026-01-16 09:01 | 46038.3757 | 2026-01-16 14:41 | 46038.6118 | 0.83426 | 0.0026036 | 94 | 30120 | Planned | Planned Outage | # Replace Poles 437298 to 437308, Tauranga Bay Rd, Kaeo
790 |  | INCD-35945-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2026-01-27 09:19 | 46049.3882 | 2026-01-27 13:55 | 46049.5799 | 0.045867 | 0.00016619 | 6 | 1656 | Planned | Planned Outage | # Vegetation Clearance, beyond Link L021, Omatarua Rd, Russell
791 |  | INCD-35951-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2026-02-26 09:00 | 46079.375 | 2026-02-26 15:58 | 46079.6653 | 1.0883 | 0.0026036 | 94 | 39292 | Planned | Planned Outage | # Replace Poles 437290, 437292, 437293, 437294, 437295, Beyond Sectionaliser S1067, Tauranga Bay, Kaeo
792 |  | INCD-35969-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2026-01-27 09:33 | 46049.3979 | 2026-01-27 15:18 | 46049.6375 | 0.40569 | 0.0013018 | 47 | 14647 | Planned | Planned Outage | # Replace Poles, Transformer near Pole 417034, Doves Bay, Waipapa
793 |  | INCD-35978-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-12-09 12:19 | 46000.5131 | 2025-12-09 13:31 | 46000.5632 | 0.15791 | 0.0021881 | 79 | 5701.1667 | Unplanned | Unknown | # Circuit Breaker CB1406 Tripped, Far North Rd, Kaitaia
794 |  | INCD-35981-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2025-12-09 12:27 | 46000.5189 | 2025-12-09 13:59 | 46000.5825 | 0.035513 | 0.00038777 | 14 | 1282.1667 | Unplanned | Vegetation | # Vegetation on Line, at Pole 429064, Church Rd, Kaitaia
795 |  | INCD-35981-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2025-12-09 12:27 | 46000.5189 | 2025-12-09 13:59 | 46000.5825 | 0.24352 | 0.002659 | 96 | 8792 | Unplanned | Vegetation | # Vegetation on Line, at Pole 429064, Church Rd, Kaitaia
796 |  | INCD-35984-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2025-12-09 13:00 | 46000.542 | 2025-12-09 14:15 | 46000.5938 | 0.31221 | 0.0041824 | 151 | 11272.15 | Planned | Planned Outage | # Extend Network to new Premise, near Pole 151902, Fairburn Rd, Kaitaia
797 |  | INCD-36002-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2025-12-11 15:06 | 46002.6292 | 2025-12-11 15:12 | 46002.6333 | 0.010636 | 0.0017727 | 64 | 384 | Unplanned | Vegetation | # Vegetation Control, near Pole 440307, Sandys Rd, Waipapa
798 |  | INCD-36023-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2025-12-12 13:27 | 46003.5604 | 2025-12-12 14:45 | 46003.6146 | 0.019444 | 0.00024928 | 9 | 702 | Unplanned | Defective Equipment | # Repair Broken Jumper, near Transformer T03765, Waiare Rd, Kaeo
799 |  | INCD-36029-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-12-12 14:28 | 46003.6028 | 2025-12-12 20:38 | 46003.8597 | 0.094505 | 0.00038777 | 14 | 3412 | Unplanned | Defective Equipment | # Line Down, near Transformer T04947, Motukiore Rd, Kaikohe
800 |  | INCD-36032-F-SOUTH ROAD | Okahu CB1105 - South Road |  | SOUTH ROAD | 2025-12-12 16:18 | 46003.6792 | 2025-12-12 20:05 | 46003.8368 | 0.365 | 0.0017727 | 64 | 13178 | Unplanned | Defective Equipment | # Repair Link L1059, Larmers Rd, Kaitaia
801 |  | INCD-36038-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-01-22 09:34 | 46044.3988 | 2026-01-22 13:56 | 46044.5805 | 1.6891 | 0.0064536 | 233 | 60983.8667 | Planned | Planned Outage | # Install Drop Out Fuses at Poles 910215 and 424215, Akatere Rd, Taipa
802 |  | INCD-36041-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-12-14 22:42 | 46005.9459 | 2025-12-14 23:23 | 46005.9743 | 0.98084 | 0.027282 | 985 | 35412.1 | Unplanned | Defective Equipment | # Cable Connection Damaged at Pole 427794, SH1, Kaitaia
803 |  | INCD-36044-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2025-12-15 03:34 | 46006.1487 | 2025-12-15 03:51 | 46006.1607 | 0.042005 | 0.0024374 | 88 | 1516.5333 | Unplanned | Unknown | # Recloser R106 Tripped, Orakau Rd, Kaikohe
804 |  | INCD-36074-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-12-17 09:31 | 46008.3969 | 2025-12-17 13:24 | 46008.5583 | 0.59001 | 0.002659 | 96 | 21301.7 | Planned | Planned Outage | # Replace Pole, Upgrade Transformer T04702, Inland Rd, Karikari Peninsula
805 |  | INCD-36080-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-12-23 09:30 | 46014.3958 | 2025-12-23 12:01 | 46014.5007 | 0.025094 | 0.00016619 | 6 | 906 | Planned | Planned Outage | # Low HV Line, Pole 419869, Okaka Rd, Kaikohe
806 |  | INCD-36095-F-OHAEAWAI | Kaikohe CB0110 - Ohaeawai |  | OHAEAWAI | 2025-12-19 06:00 | 46010.2498 | 2025-12-19 11:50 | 46010.4931 | 1.7256 | 0.02094 | 756 | 62299.4667 | Unplanned | Third Party | # Car vs Pole, at Pole 913468, SH1, Ohaewai, Kaikohe
807 |  | INCD-36101-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-12-20 01:19 | 46011.0546 | 2025-12-20 02:48 | 46011.1165 | 0.64528 | 0.032659 | 872.6697 | 23297.0567 | Unplanned | Unknown | # 33kV Circuit Breaker CB 151162 Tripped Kaitaia to Taipa 33kV, Oruru Rd, Kaitaia
808 |  | INCD-36101-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2025-12-20 01:19 | 46011.0546 | 2025-12-20 02:48 | 46011.1165 | 1.2815 | 0.050154 | 1340.1184 | 46267.4754 | Unplanned | Unknown | # 33kV Circuit Breaker CB 151162 Tripped Kaitaia to Taipa 33kV, Oruru Rd, Kaitaia
809 |  | INCD-36101-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2025-12-20 01:19 | 46011.0546 | 2025-12-20 02:48 | 46011.1165 | 3.1836 | 0.089827 | 2400.212 | 114941.9012 | Unplanned | Unknown | # 33kV Circuit Breaker CB 151162 Tripped Kaitaia to Taipa 33kV, Oruru Rd, Kaitaia
810 |  | INCD-36107-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-12-21 15:53 | 46012.6619 | 2025-12-21 16:29 | 46012.6866 | 0.07797 | 0.0021881 | 79 | 2815.0333 | Unplanned | Vegetation | # Branch on Line, near Pole 428097, Far North Rd, Kaitaia
811 |  | INCD-36110-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2025-12-22 08:25 | 46013.3505 | 2025-12-22 16:12 | 46013.675 | 0.0095684 | 2.7642e-05 | 0.99799 | 345.4569 | Unplanned | Third Party | # Car vs Pole, Pole 349055, Horeke Rd, Kaikohe
812 |  | INCD-36110-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-12-22 08:25 | 46013.3505 | 2025-12-22 16:12 | 46013.675 | 4.7689 | 0.013738 | 496.002 | 172175.8931 | Unplanned | Third Party | # Car vs Pole, Pole 349055, Horeke Rd, Kaikohe
813 |  | INCD-36113-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2026-01-12 10:32 | 46034.4389 | 2026-01-12 13:11 | 46034.5493 | 0.13652 | 0.00085863 | 31 | 4929 | Planned | Planned Outage | # Relocate Pole 437882, Te Ra Road, Waipapa
814 |  | INCD-36116-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2026-01-13 09:40 | 46035.4028 | 2026-01-13 13:38 | 46035.5681 | 0.38234 | 0.0016065 | 58 | 13804 | Planned | Planned Outage | # Install Sectionaliser S1071, Kaitaia Awaroa Rd, Kaitaia
815 |  | INCD-36119-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2025-12-23 13:13 | 46014.5507 | 2025-12-23 18:44 | 46014.7806 | 0.1084 | 0.0023266 | 84 | 3913.8333 | Unplanned | Defective Equipment | # Defective Fuse Holders, at Transformer T02675, Picadilly Rd, Kaikohe
816 |  | INCD-36122-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-12-24 11:50 | 46015.493 | 2025-12-24 20:44 | 46015.8639 | 0.099047 | 0.00083093 | 30 | 3576 | Unplanned | Third Party | # Tree through Conductor, Pole 407264, Mansbridge Rd, Broadwood
817 |  | INCD-36125-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2025-12-24 13:58 | 46015.582 | 2025-12-24 15:52 | 46015.6611 | 1.2674 | 0.019139 | 691 | 45756.6 | Unplanned | Defective Equipment | # Defective Crossarm, at Pole 402807, SH1, Kawakawa
818 |  | INCD-36128-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-12-24 16:38 | 46015.6931 | 2025-12-24 19:16 | 46015.8028 | 0.10503 | 0.00066475 | 24 | 3792 | Unplanned | Unknown | # Blown Fuse F2489, Fern Flat Rd, Taipa
819 |  | INCD-36158-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-01-21 09:42 | 46043.4042 | 2026-01-21 12:16 | 46043.5111 | 0.31138 | 0.0020219 | 73 | 11242 | Planned | Planned Outage | # Install New Spur Fuses, Poles 337054, 421676, 421722, Oruru Rd, Taipa
820 |  | INCD-36167-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-12-29 07:40 | 46020.3196 | 2025-12-29 10:00 | 46020.4163 | 0.89888 | 0.0064536 | 233 | 32453.0167 | Unplanned | Vegetation | # Vegetation tripped Line near Pole 900508, Akatere Rd, Taipa
821 |  | INCD-36176-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2025-12-29 09:42 | 46020.4045 | 2025-12-29 13:45 | 46020.5729 | 2.4161 | 0.024402 | 881 | 87229.3667 | Unplanned | Vegetation | # Tree on Line at Pole 401965, Wharau Rd, Kerikeri
822 |  | INCD-36188-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2025-12-29 09:53 | 46020.4118 | 2025-12-29 15:16 | 46020.6361 | 0.53678 | 0.0016619 | 60 | 19380 | Unplanned | Third Party | # Replace Pole due to Car vs Pole, Pole 437650, SH10, Waipapa
823 |  | INCD-36212-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2026-01-22 10:09 | 46044.4229 | 2026-01-22 15:06 | 46044.6292 | 0.065644 | 0.00060935 | 22 | 2370 | Planned | Planned Outage | # Replace R_T01315, Ruapekapeka Rd, Kawakawa
824 |  | INCD-36218-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2025-12-30 10:27 | 46021.4351 | 2025-12-30 18:22 | 46021.7653 | 5.229 | 0.054565 | 985 | 188786.05 | Unplanned | Defective Equipment | # Burnt Jumper at Pole 410757, Quarry Rd, Awanui
825 |  | INCD-36221-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-12-30 11:36 | 46021.4833 | 2025-12-30 18:15 | 46021.7604 | 2.958 | 0.019499 | 704.0014 | 106795.6504 | Unplanned | Defective Equipment | # Defective Crossarm, at Pole 425859, Lake Rd, Kaikohe
826 |  | INCD-36221-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2025-12-30 11:36 | 46021.4833 | 2025-12-30 18:15 | 46021.7604 | 0.0035107 | 2.7659e-05 | 0.99858 | 126.7496 | Unplanned | Defective Equipment | # Defective Crossarm, at Pole 425859, Lake Rd, Kaikohe
827 |  | INCD-36224-F-PUKEPOTO | Okahu CB1110 - Pukepoto |  | PUKEPOTO | 2025-12-30 12:50 | 46021.5347 | 2025-12-31 10:35 | 46022.441 | 2.1891 | 0.029498 | 1065 | 79034 | Unplanned | Vegetation | # Vegetation in Conductor, Pole 413460, Bonnett Rd, Kaitaia
828 |  | INCD-36227-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2025-12-30 12:53 | 46021.5369 | 2025-12-30 13:09 | 46021.5478 | 0.37286 | 0.023875 | 862 | 13461.5667 | Unplanned | Defective Equipment | # Defective Insulator, at Recloser R1100, Russell-Whakapara Rd, Haruru
829 |  | INCD-36233-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-12-30 13:16 | 46021.5528 | 2025-12-30 15:33 | 46021.6479 | 0.12522 | 0.00091403 | 33 | 4521 | Unplanned | Vegetation | # Vegetation through Conductor, Honeymoon Valley Rd, Taipa
830 |  | INCD-36236-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2025-12-30 14:13 | 46021.5927 | 2025-12-30 16:31 | 46021.6882 | 0.26896 | 0.0055396 | 200 | 9710.6833 | Unplanned | Defective Equipment | # Flipped Crossarm, Pole 329520, SH10, Puketona
831 |  | INCD-36242-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2025-12-30 17:06 | 46021.7122 | 2025-12-30 19:43 | 46021.8212 | 0.3794 | 0.017243 | 622.5319 | 13697.9138 | Unplanned | Vegetation | # Vegetation Caused HV, LV Clash, at Recloser R587, Te Pua Rd, Kaikohe
832 |  | INCD-36242-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2025-12-30 17:06 | 46021.7122 | 2025-12-30 19:43 | 46021.8212 | 0.69464 | 0.01954 | 705.4696 | 25079.3056 | Unplanned | Vegetation | # Vegetation Caused HV, LV Clash, at Recloser R587, Te Pua Rd, Kaikohe
833 |  | INCD-36242-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2025-12-30 17:06 | 46021.7122 | 2025-12-30 19:43 | 46021.8212 | 0.0043442 | 2.7677e-05 | 0.99925 | 156.8434 | Unplanned | Vegetation | # Vegetation Caused HV, LV Clash, at Recloser R587, Te Pua Rd, Kaikohe
834 |  | INCD-36242-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2025-12-30 17:06 | 46021.7122 | 2025-12-30 19:43 | 46021.8212 | 0.00061823 | 2.7677e-05 | 0.99925 | 22.3205 | Unplanned | Vegetation | # Vegetation Caused HV, LV Clash, at Recloser R587, Te Pua Rd, Kaikohe
835 |  | INCD-36245-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2025-12-30 16:01 | 46021.6674 | 2025-12-30 21:06 | 46021.8792 | 0.27878 | 0.00091403 | 33 | 10065 | Unplanned | Vegetation | # Tree on Line, near fuses F2255, Honeymoon Valley Rd, Taipa
836 |  | INCD-36251-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2025-12-30 17:29 | 46021.7285 | 2025-12-30 18:34 | 46021.7736 | 0.0036007 | 5.5396e-05 | 2 | 130 | Unplanned | Vegetation | # Blown Fuses due to Willow Tree, near Pole 402155
837 |  | INCD-36254-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2025-12-30 19:11 | 46021.7993 | 2025-12-30 21:26 | 46021.8931 | 0.018696 | 0.00013849 | 5 | 675 | Unplanned | Defective Equipment | # Broken Binder at Pole 430411, Dysart Rd, Herekino
838 |  | INCD-36281-F-RIVERVIEW | Waipapa 041682 - Riverview |  | RIVERVIEW | 2026-01-03 07:57 | 46025.3311 | 2026-01-03 10:28 | 46025.4361 | 2.3004 | 0.056476 | 1267 | 83052.4167 | Unplanned | Wildlife | # BirdStrike, at Pole 416662, Skudders Beach Rd, Waipapa
839 |  | INCD-36293-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2026-01-03 18:26 | 46025.7681 | 2026-01-03 22:59 | 46025.9576 | 0.068053 | 0.00024928 | 9 | 2457 | Unplanned | Unknown | # Burnt Fuses at F2023, Cook Rd, Okaihau
840 |  | INCD-36305-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-02-05 09:32 | 46058.3972 | 2026-02-05 12:45 | 46058.5312 | 0.25125 | 0.0013018 | 47 | 9071 | Planned | Planned Outage | # Install new Fuse Arm, at Pole 424318, Backriver Rd, Taipa
841 |  | INCD-36308-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-02-04 09:31 | 46057.3966 | 2026-02-04 14:19 | 46057.5962 | 2.1814 | 0.0075892 | 274 | 78756.7333 | Planned | Planned Outage | # Network Extensions, Beyond Sectionaliser S1309, Hihi Rd, Taipa
842 |  | INCD-36311-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2026-02-24 09:04 | 46077.3778 | 2026-02-24 14:02 | 46077.5847 | 0.87326 | 0.002936 | 106 | 31528 | Planned | Planned Outage | # Replacing Poles, near 437236, Tauranga Bay Rd, Kaeo
843 |  | INCD-36314-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2026-02-03 10:06 | 46056.4208 | 2026-02-03 14:34 | 46056.6069 | 0.30434 | 0.0011356 | 41 | 10988 | Unplanned | Other Cause | # Replace Crossarms, Pole 211773, Waiotemarama Gorge Rd, Omanaia
844 |  | INCD-36317-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2026-02-10 08:37 | 46063.359 | 2026-02-10 14:22 | 46063.5986 | 0.16245 | 0.00047086 | 17 | 5865 | Planned | Planned Outage | # Pole Replacement, near Link L192, Jordan Rd, Kaikohe
845 |  | INCD-36329-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-01-27 09:34 | 46049.3986 | 2026-01-27 13:59 | 46049.5826 | 0.82207 | 0.0031021 | 112 | 29680 | Planned | Planned Outage | # Network Additions, Beyond Switch 184, Oruru Rd, Taipa
846 |  | INCD-36338-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2026-01-20 10:00 | 46042.4168 | 2026-01-20 13:52 | 46042.5776 | 2.8984 | 0.012519 | 452 | 104645.5333 | Planned | Planned Outage | # Broken Crossarm at Pole 417746, Redcliffs Rd, Waipapa
847 |  | INCD-36341-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2026-01-28 09:34 | 46050.3986 | 2026-01-28 14:55 | 46050.6215 | 1.9108 | 0.0063151 | 228 | 68986 | Planned | Planned Outage | # Replace Multiple Crossarms, Beyond Switch 758, MacFarlane Street, Kawakawa
848 |  | INCD-36344-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2026-01-29 10:02 | 46051.4182 | 2026-01-29 13:32 | 46051.5636 | 0.11013 | 0.00052626 | 19 | 3976.0667 | Planned | Planned Outage | # Remove Motorised Switch 1231M, SH1, Kaitaia
849 |  | INCD-36368-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-01-08 07:51 | 46030.3271 | 2026-01-08 10:13 | 46030.4259 | 0.12218 | 0.00085863 | 31 | 4411.3 | Unplanned | Vegetation | # Branch on Line at Pole 415482, Rangi Point Rd, Kaitaia
850 |  | INCD-36374-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2026-01-30 09:09 | 46052.3812 | 2026-01-30 13:07 | 46052.5465 | 0.15455 | 0.00066475 | 24 | 5580 | Planned | Planned Outage | # SWER Maintenance, Beyond Fuse F2032, Peria Valley Rd, Kaitaia
851 |  | INCD-36377-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2026-01-08 09:23 | 46030.391 | 2026-01-08 11:38 | 46030.4847 | 0.0037392 | 2.7698e-05 | 1 | 135 | Unplanned | Unknown | # Fuse L588 Blown, Te Tio Rd, Umawera
852 |  | INCD-36380-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2026-01-08 14:23 | 46030.5996 | 2026-01-08 15:08 | 46030.6306 | 0.21732 | 0.0049302 | 178 | 7846.1167 | Unplanned | Wildlife | # Bird Strike at T1317M, Cable Bay Block Rd, Taipa
853 |  | INCD-36389-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2026-01-29 09:06 | 46051.3792 | 2026-01-29 11:55 | 46051.4965 | 0.11702 | 0.00069244 | 25 | 4225 | Planned | Planned Outage | # Vegetation Removal, Beyond Link L522, Kawakawa
854 |  | INCD-36407-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2026-01-10 11:29 | 46032.4784 | 2026-01-10 12:36 | 46032.5252 | 0.5542 | 0.0083093 | 300 | 20008.9667 | Unplanned | Defective Equipment | # Broken Crossarm, at Pole 410431, Kapiro Rd, Kerikeri
855 |  | INCD-36413-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2026-02-09 09:10 | 46062.3819 | 2026-02-09 11:41 | 46062.4868 | 0.068995 | 0.00085863 | 31 | 2491 | Planned | Planned Outage | # Replace Crossarms, at Transformer T02897, Peria Valley Rd, Kaitaia
856 |  | INCD-36419-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2026-01-12 03:31 | 46034.1465 | 2026-01-12 05:38 | 46034.2347 | 0.33417 | 0.0026313 | 95 | 12065 | Unplanned | Unknown | # Blown Fuses at Switch S156, Pupuke Mangapa Rd, Kaeo
857 |  | INCD-36422-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2026-01-12 13:38 | 46034.5681 | 2026-01-12 15:26 | 46034.6431 | 0.04487 | 0.00041547 | 15 | 1620 | Unplanned | Third Party | # Truck vs Line, at Pole 427901, Gill Rd, Kaitaia
858 |  | INCD-36428-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2026-01-13 10:19 | 46035.4299 | 2026-01-13 11:34 | 46035.4819 | 0.03116 | 0.00041547 | 15 | 1125 | Unplanned | Defective Equipment | # Replacing Fuse at R_T01280, Gill Rd, Kaitaia
859 |  | INCD-36476-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2026-01-14 16:11 | 46036.6743 | 2026-01-14 17:57 | 46036.7479 | 0.27653 | 0.002659 | 96 | 9984 | Unplanned | Vegetation | # Vegetation on Line Blew Fuse F2244 at Onekura Rd, Waipapa
860 |  | INCD-36488-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2026-01-18 09:32 | 46040.3972 | 2026-01-18 09:43 | 46040.4049 | 0.0067029 | 0.00060935 | 22 | 242 | Planned | Planned Outage | # Remove Faulty Ring Main RM218, Whangatane Dr, Kaitaia
861 |  | INCD-36512-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2026-01-17 02:39 | 46039.1105 | 2026-01-17 04:40 | 46039.1944 | 1.6146 | 0.023405 | 606 | 58292.9167 | Unplanned | Unknown | # Circuit Breaker 131132 Tripped, Lamb Rd, Pukenui
862 |  | INCD-36515-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2026-01-17 12:28 | 46039.5194 | 2026-01-17 19:30 | 46039.8125 | 0.37584 | 0.0068413 | 239 | 13569.45 | Unplanned | Vegetation | # Repair Broken Conductor, at Pole 422172, Kaitaia Awaroa Rd, Kaitaia
863 |  | INCD-36530-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2026-01-18 09:34 | 46040.3986 | 2026-01-18 14:18 | 46040.5958 | 0.66862 | 0.0023543 | 85 | 24140 | Unplanned | Vegetation | # Lines Down due to Vegetation, at Pole 451314, Rawhiti Rd, Kawakawa
864 |  | INCD-36539-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2026-01-18 09:39 | 46040.4021 | 2026-01-18 18:16 | 46040.7611 | 0.36428 | 0.002659 | 96 | 13152 | Unplanned | Vegetation | # Vegetation Blew Fuse F2244, Onekura Rd, Waipapa
865 |  | INCD-36542-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2026-01-18 09:51 | 46040.4104 | 2026-01-18 14:17 | 46040.5951 | 0.07916 | 0.00052626 | 12 | 2858 | Unplanned | Other Cause | # Fuse F2303 Blown, Caused by Line Clash due to Street Lighting, Totara North Rd, Kaeo
866 |  | INCD-36545-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2026-01-18 14:05 | 46040.5868 | 2026-01-18 19:15 | 46040.8021 | 0.37195 | 0.0025482 | 46 | 13429 | Unplanned | Vegetation | # Line Down due to Trees, between Poles 405080 to 405081, Waikare Rd, Kawakawa
867 |  | INCD-36551-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-01-18 14:34 | 46040.6069 | 2026-01-18 20:10 | 46040.8403 | 0.10237 | 0.00030468 | 11 | 3696 | Unplanned | Adverse Weather | # Repair Jumper, at Fuse F_T01519, West Coast Rd, Kaitaia
868 |  | INCD-36554-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2026-01-18 14:41 | 46040.6118 | 2026-01-20 12:55 | 46042.5382 | 0.61467 | 0.00022158 | 8 | 22192 | Unplanned | Defective Equipment | # Line Down, at Pole 404703, Paroa Rd, Kawakawa
869 |  | INCD-36557-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2026-02-11 09:06 | 46064.3792 | 2026-02-11 14:49 | 46064.6174 | 0.39901 | 0.0011633 | 42 | 14406 | Planned | Planned Outage | # Vegetation Clearance, Beyond Links L512, Otangaroa Rd, Kaeo
870 |  | INCD-36560-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2026-01-16 22:19 | 46038.9301 | 2026-01-18 14:07 | 46040.5882 | 0.53648 | 0.010442 | 303 | 19369.15 | Unplanned | Third Party | # Car vs Pole, at Pole 205220, Awanui, Kaitaia
871 |  | INCD-36569-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2026-01-19 12:44 | 46041.5306 | 2026-01-19 15:44 | 46041.6558 | 0.15986 | 0.0078662 | 202 | 5771.5 | Unplanned | Vegetation | # Branch on Line, at Pole 440775, Bulls Gorge, Mt Pokaka
872 |  | INCD-36578-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2026-01-19 12:14 | 46041.5097 | 2026-01-20 21:49 | 46042.909 | 0.16209 | 0.00060935 | 22 | 5852 | Unplanned | Third Party | # Trees through Line, near Ruapekapeka Rd, Kawakawa
873 |  | INCD-36584-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2026-01-20 10:24 | 46042.4333 | 2026-01-20 11:54 | 46042.4958 | 0.1022 | 0.0011356 | 41 | 3690 | Unplanned | Defective Equipment | # Jumper Off Pole 211773, Waiotemarama Gorge Rd, Omanaia
874 |  | INCD-36590-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2026-01-30 10:12 | 46052.425 | 2026-01-30 11:39 | 46052.4854 | 0.18073 | 0.0020773 | 75 | 6525 | Planned | Planned Outage | # Replace Rotten Crossarms, at Pole 440500, Valencia Lane, Mt Pokaka
875 |  | INCD-36593-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-01-21 09:07 | 46043.3799 | 2026-01-22 15:36 | 46044.65 | 0.38835 | 0.00096942 | 14 | 14021 | Unplanned | Wildlife | # Bird Strike, at Pole 407491, South Rd, Kaitaia
876 |  | INCD-36596-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2026-02-09 09:43 | 46062.4049 | 2026-02-09 11:59 | 46062.4993 | 0.033902 | 0.00024928 | 9 | 1224 | Planned | Planned Outage | # Install Poles near Pole 437054, Stanners Rd, Waipapa
877 |  | INCD-36599-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2026-01-21 10:34 | 46043.4403 | 2026-01-21 15:50 | 46043.6597 | 0.078772 | 0.00024928 | 9 | 2844 | Unplanned | Defective Equipment | # Replace Crossarms, on Poles 434796, 436797, Jackson Rd, Omanaia
878 |  | INCD-36602-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2026-01-21 15:19 | 46043.6379 | 2026-01-21 17:17 | 46043.7201 | 0.42569 | 0.0037392 | 135 | 15369.2333 | Unplanned | Unknown | # Sectionaliser S1055 Tripped, Manawaora Rd, Kawakawa
879 |  | INCD-36620-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2026-01-21 22:33 | 46043.9396 | 2026-01-22 11:08 | 46044.4639 | 0.083398 | 0.00011079 | 4 | 3011 | Unplanned | Vegetation | # Tree through Line, at Pole 440306, Sandys Rd, Waipapa
880 |  | INCD-36626-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2026-01-22 07:38 | 46044.3184 | 2026-01-22 12:23 | 46044.5163 | 0.61677 | 0.004764 | 172 | 22267.7 | Unplanned | Defective Equipment | # Broken Crossarm, Line, Beyond 1701 Puketona Rd, Mt Pokaka
881 |  | INCD-36629-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2026-01-22 08:28 | 46044.3529 | 2026-01-22 11:27 | 46044.4771 | 0.49016 | 0.0059827 | 216 | 17696.6667 | Unplanned | Defective Equipment | # Broken Jumpers at Link L016, Hillcrest Rd, Kaikohe
882 |  | INCD-36632-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2026-01-22 13:22 | 46044.5569 | 2026-01-22 14:15 | 46044.5938 | 0.12478 | 0.0023543 | 85 | 4505 | Unplanned | Vegetation | # Trees Burning in Lines near Pole 912115, Rawhiti Rd, Kawakawa
883 |  | INCD-36638-F-TAU BLOCK | Moerewa 031372 - Tau Block |  | TAU BLOCK | 2026-02-11 09:31 | 46064.3967 | 2026-02-11 13:48 | 46064.575 | 0.0071114 | 2.7698e-05 | 1 | 256.75 | Planned | Planned Outage | # Replace Poles 404364 and 404365, Saies Rd, Moerewa
884 |  | INCD-36641-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2026-02-16 09:42 | 46069.4042 | 2026-02-16 10:23 | 46069.4326 | 0.011356 | 0.00027698 | 10 | 410 | Planned | Planned Outage | # New Connection at T03966, Inland Rd, Taipa
885 |  | INCD-36647-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2026-02-05 10:35 | 46058.441 | 2026-02-05 13:09 | 46058.5479 | 0.051185 | 0.00033237 | 12 | 1848 | Planned | Planned Outage | # Replace Crossarms, at Pole 420063, Horeke Rd, Kaikohe
886 |  | INCD-36656-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2026-02-18 09:02 | 46071.3764 | 2026-02-18 15:35 | 46071.6493 | 0.64824 | 0.0023543 | 85 | 23404 | Planned | Planned Outage | # Pole Replacement, TX Upgrade T03478, Wiroa Rd, Mt Pokaka
887 |  | INCD-36659-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2026-03-25 09:01 | 46106.3757 | 2026-03-25 16:44 | 46106.6972 | 1.145 | 0.0026036 | 94 | 41338 | Planned | Planned Outage | # Replace Poles 437304 to 437308, Tauranga Bay Rd, Kaeo
888 |  | INCD-36662-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2026-01-24 01:19 | 46046.0552 | 2026-01-24 06:53 | 46046.2868 | 0.0028136 | 5.53e-05 | 1.7108 | 101.5814 | Unplanned | Vegetation | # Tree on Line, Fuse Blown, at Pole 419846, Okaka Rd, Kaikohe
889 |  | INCD-36662-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2026-01-24 01:19 | 46046.0552 | 2026-01-24 06:53 | 46046.2868 | 2.5914 | 0.016009 | 495.2892 | 93559.5019 | Unplanned | Vegetation | # Tree on Line, Fuse Blown, at Pole 419846, Okaka Rd, Kaikohe
890 |  | INCD-36665-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2026-01-24 06:11 | 46046.2576 | 2026-01-24 10:50 | 46046.4514 | 0.36237 | 0.0013572 | 49 | 13083 | Unplanned | Unknown | # SWER Recloser T_T01335 Tripped, Wekaweka Rd, Omanaia
891 |  | INCD-36674-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2026-01-24 13:38 | 46046.5681 | 2026-01-24 14:23 | 46046.5993 | 0.077277 | 0.0017173 | 62 | 2790 | Unplanned | Defective Equipment | # Flipped Crossarm, at Pole 432345, Far North Rd, Pukenui
892 |  | INCD-36677-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2026-01-24 13:08 | 46046.5472 | 2026-01-24 16:39 | 46046.6937 | 0.064287 | 0.00030468 | 11 | 2321 | Unplanned | Vegetation | # Line Stuck in Tree, at Pole 429552, Puriri Rd, Kaitaia
893 |  | INCD-36683-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-01-24 13:32 | 46046.5639 | 2026-01-24 19:09 | 46046.7979 | 0.14001 | 0.00041547 | 15 | 5055 | Unplanned | Unknown | # Fuse F2096 Blown, Awaroa Rd, Broadwood
894 |  | INCD-36689-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-01-24 19:21 | 46046.806 | 2026-01-25 16:00 | 46047.6667 | 0.69023 | 0.0093895 | 339 | 24919.9167 | Unplanned | Vegetation | # Line Down at Pole 492495, Kohumaru Rd, Taipa
895 |  | INCD-36695-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2026-01-25 05:29 | 46047.2284 | 2026-01-25 07:53 | 46047.3284 | 1.8025 | 0.013738 | 496.002 | 65078.0102 | Unplanned | Unknown | # Recloser R694 Tripped, Settlers Way, Kaikohe
896 |  | INCD-36695-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2026-01-25 05:29 | 46047.2284 | 2026-01-25 07:53 | 46047.3284 | 0.0025876 | 2.7642e-05 | 0.99799 | 93.4231 | Unplanned | Unknown | # Recloser R694 Tripped, Settlers Way, Kaikohe
897 |  | INCD-36704-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2026-01-26 04:07 | 46048.1714 | 2026-01-26 07:42 | 46048.3211 | 0.0031849 | 5.5284e-05 | 0.99799 | 114.9894 | Unplanned | Vegetation | # Trees in Line at Pole 419792, Utakura Valley Rd, Kaikohe
898 |  | INCD-36704-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2026-01-26 04:07 | 46048.1714 | 2026-01-26 07:42 | 46048.3211 | 2.7101 | 0.027476 | 496.002 | 97844.5773 | Unplanned | Vegetation | # Trees in Line at Pole 419792, Utakura Valley Rd, Kaikohe
899 |  | INCD-36713-F-MATAURI BAY | Kaeo 191732 - Matauri Bay |  | MATAURI BAY | 2026-02-02 10:15 | 46055.4271 | 2026-02-02 13:26 | 46055.5597 | 0.037032 | 0.00019388 | 7 | 1337 | Planned | Planned Outage | # Relocate Pole 907223, Wainui Rd, Kaeo
900 |  | INCD-36719-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2026-02-18 09:36 | 46071.4 | 2026-02-18 13:24 | 46071.5583 | 0.012602 | 5.5396e-05 | 2 | 455 | Planned | Planned Outage | # Cross Arm Replacements beyond Link L305, Sandhills Rd, Kaitaia
901 |  | INCD-36722-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2026-02-20 09:32 | 46073.3972 | 2026-02-20 13:32 | 46073.5639 | 0.11965 | 0.00049856 | 18 | 4320 | Planned | Planned Outage | # Install New Conductor, Beyond Link 305, Sandhills Rd, Kaitaia
902 |  | INCD-36728-F-TI BAY | Haruru CB0606 - Ti Bay |  | TI BAY | 2026-02-23 10:01 | 46076.417 | 2026-02-23 13:18 | 46076.5544 | 0.67958 | 0.0034345 | 124 | 24535.4667 | Planned | Planned Outage | # Network Upgrade, beyond S1021, Puketona Rd, Haruru
903 |  | INCD-36731-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2026-02-03 09:34 | 46056.3986 | 2026-02-03 10:33 | 46056.4396 | 0.049025 | 0.00083093 | 30 | 1770 | Planned | Planned Outage | # Straightening Pole 420463, West Coast Rd, Kaikohe
904 |  | INCD-36743-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2026-01-30 04:56 | 46052.2056 | 2026-01-30 13:27 | 46052.5604 | 0.43524 | 0.00085863 | 31 | 15714 | Unplanned | Defective Equipment | # Replace SWER Transformer T05695, Waima Valley Rd, Omanaia
905 |  | INCD-36761-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-02-24 09:31 | 46077.3967 | 2026-02-24 13:57 | 46077.5809 | 0.53635 | 0.0020219 | 73 | 19364.4667 | Planned | Planned Outage | # Replace Pole, Crossarms, Switch, at Pole 415318, West Coast Rd, Kaitaia
906 |  | INCD-36764-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2026-01-30 21:15 | 46052.8854 | 2026-01-31 03:20 | 46053.1389 | 0.090987 | 0.00024928 | 9 | 3285 | Unplanned | Vegetation | # Replace Conductor, Beyond Fuse F2236, Marlow Rd, Kawakawa
907 |  | INCD-36767-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2026-02-09 10:16 | 46062.4278 | 2026-02-09 15:13 | 46062.634 | 0.031409 | 0.00011079 | 4 | 1134 | Planned | Planned Outage | # Replace Transformer Pole 423739, Maromaku Rd, Kawakawa
908 |  | INCD-36770-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2026-02-01 09:20 | 46054.3889 | 2026-02-01 11:27 | 46054.4771 | 0.10553 | 0.00083093 | 30 | 3810 | Unplanned | Defective Equipment | # Replace Burnt Link L738, Taratara Rd, Kaeo
909 |  | INCD-36782-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2026-02-02 09:38 | 46055.4015 | 2026-02-02 11:03 | 46055.4604 | 0.19267 | 0.004127 | 84 | 6956.0833 | Unplanned | Vegetation | # Branch on Line, at Transformer T04142, Mataraua Rd, Kaikohe
910 |  | INCD-36797-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2026-02-02 13:45 | 46055.5728 | 2026-02-02 15:18 | 46055.6378 | 0.85289 | 0.012519 | 452 | 30792.8 | Unplanned | Vegetation | # Recloser R270 Tripped, Redcliffs Rd, Waipapa
911 |  | INCD-36800-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2026-02-16 09:04 | 46069.3778 | 2026-02-16 15:00 | 46069.625 | 0.54232 | 0.0015234 | 55 | 19580 | Planned | Planned Outage | # Vegetation Control, Beyond Switch 470, Spains Rd, Awanui
912 |  | INCD-36806-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2026-02-02 21:33 | 46055.8979 | 2026-02-03 02:29 | 46056.1035 | 0.081985 | 0.00027698 | 10 | 2960 | Unplanned | Defective Equipment | # Broken Crossarm, at Pole 412848, Mangataipa Rd, Kaikohe
913 |  | INCD-36812-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2026-02-27 10:00 | 46080.4169 | 2026-02-27 15:51 | 46080.6604 | 0.66097 | 0.0022158 | 80 | 23863.7 | Planned | Planned Outage | # Replace Poles, Crossarms, at Pole 409910, Hospital Rd, Kaeo
914 |  | INCD-36818-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2026-03-05 09:29 | 46086.3951 | 2026-03-05 12:42 | 46086.5292 | 0.085531 | 0.00044316 | 16 | 3088 | Planned | Planned Outage | # Network Extension, at Pole 440123, Waiare Rd, Kaeo
915 |  | INCD-36824-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2026-02-25 10:00 | 46078.4169 | 2026-02-25 13:39 | 46078.5684 | 0.85813 | 0.0039331 | 142 | 30982.0333 | Planned | Planned Outage | # Replace Crossarms, Clear Vegetation, at Pole 437784, Otaha Road, Waipapa
916 |  | INCD-36827-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2026-03-06 09:07 | 46087.3799 | 2026-03-06 12:43 | 46087.5299 | 0.78324 | 0.0037669 | 136 | 28278 | Planned | Planned Outage | # Replace Multiple Crossarms Beyond Switch 079, Okahu Rd, Kaitaia
917 |  | INCD-36830-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2026-02-20 11:40 | 46073.4861 | 2026-02-20 13:30 | 46073.5625 | 0.018281 | 0.00016619 | 6 | 660 | Planned | Planned Outage | # Re-sag Lines between Poles 419846 & 419847, Okaka Rd, Kaikohe
918 |  | INCD-36839-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2026-02-19 10:02 | 46072.4181 | 2026-02-19 13:35 | 46072.566 | 0.23598 | 0.0011079 | 40 | 8520 | Planned | Planned Outage | # Broken Pole 437169, Mahinepua Rd, Kaeo
919 |  | INCD-36842-F-TE KEMARA AVE | Haruru CB0605 - Te Kemara Ave |  | TE KEMARA AVE | 2026-02-24 21:03 | 46077.8771 | 2026-02-25 01:17 | 46078.0535 | 0.0070352 | 2.7698e-05 | 1 | 254 | Planned | Planned Outage | # Commission Ring Main RM289, Puketona Rd, Haruru
920 |  | INCD-36845-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2026-02-18 10:16 | 46071.4278 | 2026-02-18 15:04 | 46071.6278 | 0.37492 | 0.0013018 | 47 | 13536 | Planned | Planned Outage | # Pole Replacement, Pole 435329, Omanaia Rd, Omanaia
921 |  | INCD-36851-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2026-02-27 09:30 | 46080.3958 | 2026-02-27 15:28 | 46080.6444 | 1.9683 | 0.01083 | 295 | 71065 | Planned | Planned Outage | # Replace Pole, Cable Rise, at Transformer T01834, Reef View Rd, Okahu Rd
922 |  | INCD-36854-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2026-02-05 14:31 | 46058.6049 | 2026-02-05 16:57 | 46058.7063 | 0.0040439 | 2.7698e-05 | 1 | 146 | Unplanned | Unknown | # Replace Blown Fuse, L588, Kaikohe
923 |  | INCD-36866-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2026-02-06 16:53 | 46059.7033 | 2026-02-06 22:33 | 46059.9396 | 0.88604 | 0.0026036 | 94 | 31989.7667 | Unplanned | Third Party | # Car vs Pole, Pole 333521, SH10, Cable Bay, Taipa
924 |  | INCD-36872-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2026-02-09 11:22 | 46062.4737 | 2026-02-09 15:01 | 46062.6257 | 0.37471 | 0.005041 | 182 | 13528.55 | Unplanned | Third Party | # Third Party Contact at Pole 411624, Signal Rd, Waipapa
925 |  | INCD-36893-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-02-10 17:07 | 46063.7132 | 2026-02-10 20:07 | 46063.8382 | 0.095613 | 0.00074784 | 27 | 3452 | Unplanned | Vegetation | # Tree through Line, at Pole 201723, Proctor Road, Kaitaia
926 |  | INCD-36896-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2026-02-10 18:10 | 46063.7569 | 2026-02-11 06:41 | 46064.2785 | 0.0066475 | 0.00022158 | 8 | 240 | Unplanned | Defective Equipment | # Faulty Fuse Arm at T04558, Monument Rd, Kawakawa
927 |  | INCD-36899-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2026-02-10 23:13 | 46063.9675 | 2026-02-11 02:31 | 46064.1045 | 0.0053774 | 2.7664e-05 | 0.84736 | 194.1458 | Unplanned | Defective Equipment | # Defective Link L047, Settlers Way, Kaikohe
928 |  | INCD-36899-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2026-02-10 23:13 | 46063.9675 | 2026-02-11 02:31 | 46064.1045 | 2.815 | 0.022989 | 704.1526 | 101634.5209 | Unplanned | Defective Equipment | # Defective Link L047, Settlers Way, Kaikohe
929 |  | INCD-36911-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2026-02-25 07:43 | 46078.3215 | 2026-02-25 15:00 | 46078.625 | 0.048416 | 0.00011079 | 4 | 1748 | Planned | Planned Outage | # Vegetation Clearance, beyond Link L208, Ruapekapeka Rd, Kawakawa
930 |  | INCD-36923-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2026-02-12 10:25 | 46065.4341 | 2026-02-12 13:58 | 46065.5819 | 0.79361 | 0.036395 | 796.6919 | 28652.5 | Unplanned | Unknown | # Broken Jumper L192, Jordan Rd, Kaikohe
931 |  | INCD-36923-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2026-02-12 10:25 | 46065.4341 | 2026-02-12 13:58 | 46065.5819 | 3.109 | 0.029969 | 656.0279 | 112248.4667 | Unplanned | Unknown | # Broken Jumper L192, Jordan Rd, Kaikohe
932 |  | INCD-36923-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2026-02-12 10:25 | 46065.4341 | 2026-02-12 13:58 | 46065.5819 | 0.53785 | 0.010581 | 231.6106 | 19418.5167 | Unplanned | Unknown | # Broken Jumper L192, Jordan Rd, Kaikohe
933 |  | INCD-36923-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2026-02-12 10:25 | 46065.4341 | 2026-02-12 13:58 | 46065.5819 | 0.98604 | 0.020496 | 448.6697 | 35599.9667 | Unplanned | Unknown | # Broken Jumper L192, Jordan Rd, Kaikohe
934 |  | INCD-36935-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2026-02-12 14:04 | 46065.5861 | 2026-02-12 15:18 | 46065.6375 | 0.026645 | 0.00036007 | 13 | 962 | Unplanned | Wildlife | # Blown Fuse F2147, Dick Urlich Rd, Taipa
935 |  | INCD-36938-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2026-02-12 15:06 | 46065.6292 | 2026-02-12 20:44 | 46065.8639 | 0.13107 | 0.00038777 | 14 | 4732 | Unplanned | Vegetation | # Fuse 2013 Blown by Vegetation, Ramsey Rd, Omanaia
936 |  | INCD-36947-F-POKAPU | Moerewa 031312 - Pokapu |  | POKAPU | 2026-02-12 21:17 | 46065.8868 | 2026-02-12 23:03 | 46065.9604 | 0.011744 | 0.00011079 | 4 | 424 | Unplanned | Defective Equipment | # Defective Fuse S143, Lucas Rd, Moerewa
937 |  | INCD-36950-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2026-02-13 05:24 | 46066.225 | 2026-02-13 10:28 | 46066.4361 | 0.34678 | 0.0020219 | 42 | 12520 | Unplanned | Lightning | # Lightning Arrestors Blown, near T01190, Te Ranga Rd, Kaeo
938 |  | INCD-36956-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.58143 | 0.013102 | 473.0377 | 20991.9691 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
939 |  | INCD-36956-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.18962 | 0.0041827 | 151.012 | 6845.8885 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
940 |  | INCD-36956-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.92045 | 0.020304 | 733.0584 | 33232.0285 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
941 |  | INCD-36956-F-OXFORD STREET | Okahu CB1108 - Oxford Street |  | OXFORD STREET | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.42819 | 0.0098058 | 354.0282 | 15459.2538 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
942 |  | INCD-36956-F-KAITAIA WEST | Okahu CB1106 - Kaitaia West |  | KAITAIA WEST | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.18888 | 0.0043212 | 156.0124 | 6819.4864 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
943 |  | INCD-36956-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 1.5013 | 0.032741 | 1182.0941 | 54202.8292 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
944 |  | INCD-36956-F-VICTORIA VALLEY | Kaitaia Transmission 151802 - Victoria Valley |  | VICTORIA VALLEY | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.23608 | 0.0052076 | 188.015 | 8523.3579 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
945 |  | INCD-36956-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.79224 | 0.016952 | 612.0487 | 28603.1197 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
946 |  | INCD-36956-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.090413 | 0.0019944 | 72.0057 | 3264.2647 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
947 |  | INCD-36956-F-SOUTH ROAD | Okahu CB1105 - South Road |  | SOUTH ROAD | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.077412 | 0.0017728 | 64.0051 | 2794.8933 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
948 |  | INCD-36956-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 1.2056 | 0.027312 | 986.0785 | 43525.4633 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
949 |  | INCD-36956-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.70538 | 0.015983 | 577.046 | 25466.9987 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
950 |  | INCD-36956-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.8738 | 0.018697 | 675.0538 | 31547.5585 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
951 |  | INCD-36956-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 2.06 | 0.044929 | 1622.1292 | 74374.7319 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
952 |  | INCD-36956-F-REDAN ROAD | Okahu CB1107 - Redan Road |  | REDAN ROAD | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 0.85637 | 0.019612 | 708.0564 | 30918.5075 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
953 |  | INCD-36956-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 1.3565 | 0.031052 | 1121.0893 | 48975.1053 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
954 |  | INCD-36956-F-PUKEPOTO | Okahu CB1110 - Pukepoto |  | PUKEPOTO | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 1.2882 | 0.0295 | 1065.0848 | 46508.7719 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
955 |  | INCD-36956-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2026-02-13 11:18 | 46066.4711 | 2026-02-13 12:09 | 46066.5062 | 2.3069 | 0.050303 | 1816.1446 | 83288.5048 | Unplanned | Lightning | # Lightning Stike Damaged Switch 151087, Kaitaia 33kV Switchyard, Kaitaia
956 |  | INCD-36971-F-POKAPU | Moerewa 031312 - Pokapu |  | POKAPU | 2026-02-12 21:17 | 46065.8868 | 2026-02-13 19:51 | 46066.8271 | 0.14029 | 0.00011079 | 4 | 5065 | Unplanned | Defective Equipment | # Jumper Broken at Transformer T04161, Lucas Rd, Moerewa
957 |  | INCD-36992-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-03-04 09:31 | 46085.3966 | 2026-03-04 14:43 | 46085.6133 | 3.1207 | 0.0099989 | 361 | 112668.1 | Planned | Planned Outage | # Replacing Xarms, Poles, Beyond Sectionaliser S1047, SH10, Taipa
958 |  | INCD-36998-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2026-02-15 07:40 | 46068.3195 | 2026-02-15 12:27 | 46068.5188 | 1.3617 | 0.012132 | 438 | 49163.1 | Unplanned | Third Party | # Car vs Pole, at Pole 406597, SH12, Waima
959 |  | INCD-37001-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2026-02-15 14:15 | 46068.594 | 2026-02-15 14:44 | 46068.6137 | 0.070754 | 0.0024928 | 90 | 2554.5 | Unplanned | Vegetation | # Trees in Line, at Pole 436411, Waimate Rd, Waimate North
960 |  | INCD-37010-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2026-03-03 08:42 | 46084.3625 | 2026-03-03 11:02 | 46084.4597 | 0.11245 | 0.00080324 | 29 | 4060 | Planned | Planned Outage | # Isolation for Omanaia 33kV Pole Replacements, near Switch 451, Rakauwahia Rd, Omanaia
961 |  | INCD-37013-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2026-02-16 15:00 | 46069.6247 | 2026-02-16 15:07 | 46069.63 | 0.12673 | 0.016785 | 606 | 4575.3 | Unplanned | Unknown | # Circuit Breaker 131012 Tripped, Lamb Road, Pukenui
962 |  | INCD-37013-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2026-02-16 15:00 | 46069.6247 | 2026-02-16 15:07 | 46069.63 | 0.14115 | 0.018696 | 675 | 5096.25 | Unplanned | Unknown | # Circuit Breaker 131012 Tripped, Lamb Road, Pukenui
963 |  | INCD-37028-F-WHANGAROA | Kaeo 191722 - Whangaroa |  | WHANGAROA | 2026-02-16 16:16 | 46069.6778 | 2026-02-16 18:15 | 46069.7604 | 0.029664 | 0.00024928 | 9 | 1071 | Unplanned | Defective Equipment | # Replace Crossarm at Pole 436945, Wainui Rd, Kaeo
964 |  | INCD-37031-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2026-02-16 16:19 | 46069.68 | 2026-02-16 17:33 | 46069.7313 | 0.39282 | 0.005318 | 192 | 14182.4 | Unplanned | Unknown | # Sectionaliser S1044 Tripped, Opito Bay Rd, Waipapa
965 |  | INCD-37040-F-REDAN ROAD | Okahu CB1107 - Redan Road |  | REDAN ROAD | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.1886 | 0.019612 | 708.0565 | 6809.0353 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
966 |  | INCD-37040-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.1537 | 0.015983 | 577.046 | 5549.1715 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
967 |  | INCD-37040-F-VICTORIA VALLEY | Kaitaia Transmission 151802 - Victoria Valley |  | VICTORIA VALLEY | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.050079 | 0.0052076 | 188.015 | 1808.0489 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
968 |  | INCD-37040-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.26326 | 0.02734 | 987.0787 | 9504.7244 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
969 |  | INCD-37040-F-SOUTH ROAD | Okahu CB1105 - South Road |  | SOUTH ROAD | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.017048 | 0.0017728 | 64.0051 | 615.506 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
970 |  | INCD-37040-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.33172 | 0.044929 | 1622.1293 | 11976.5324 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
971 |  | INCD-37040-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.29964 | 0.031052 | 1121.0894 | 10818.375 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
972 |  | INCD-37040-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.37241 | 0.050165 | 1811.1444 | 13445.5763 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
973 |  | INCD-37040-F-KAITAIA WEST | Okahu CB1106 - Kaitaia West |  | KAITAIA WEST | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.0419 | 0.0043212 | 156.0124 | 1512.7634 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
974 |  | INCD-37040-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.25304 | 0.018697 | 675.0538 | 9135.5841 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
975 |  | INCD-37040-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.22717 | 0.016786 | 606.0483 | 8201.7244 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
976 |  | INCD-37040-F-PUKEPOTO | Okahu CB1110 - Pukepoto |  | PUKEPOTO | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.28369 | 0.0295 | 1065.0849 | 10242.4049 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
977 |  | INCD-37040-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.040223 | 0.0041827 | 151.012 | 1452.2095 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
978 |  | INCD-37040-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.24133 | 0.032631 | 1178.0939 | 8712.8237 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
979 |  | INCD-37040-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.126 | 0.013102 | 473.0377 | 4548.9742 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
980 |  | INCD-37040-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.19525 | 0.020304 | 733.0584 | 7049.4674 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
981 |  | INCD-37040-F-OXFORD STREET | Okahu CB1108 - Oxford Street |  | OXFORD STREET | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.094298 | 0.0098058 | 354.0282 | 3404.5177 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
982 |  | INCD-37040-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2026-02-17 12:27 | 46070.5186 | 2026-02-17 12:49 | 46070.5339 | 0.019179 | 0.0019944 | 72.0057 | 692.4443 | Unplanned | Defective Equipment | # Circuit Breaker 151172 Tripped Northern Network, SH1, Kaitaia
983 |  | INCD-37043-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2026-02-17 14:47 | 46070.6163 | 2026-02-17 21:18 | 46070.8875 | 0.55612 | 0.018918 | 347 | 20078.0667 | Unplanned | Third Party | # Replace Pole 416206 Hit By Tracker, Ngapuhi Rd, Kaikohe
984 |  | INCD-37061-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2026-03-11 09:26 | 46092.3932 | 2026-03-11 11:17 | 46092.4698 | 0.097836 | 0.00088633 | 32 | 3532.2667 | Planned | Planned Outage | # Install Links, Connect Cable, Pole 405345, Duddy Rd, Omanaia
985 |  | INCD-37064-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2026-03-04 09:52 | 46085.4111 | 2026-03-04 15:17 | 46085.6368 | 1.9264 | 0.0059273 | 214 | 69550 | Planned | Planned Outage | # Replaced Recloser R071. Paihia Rd, Haruru
986 |  | INCD-37070-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2026-02-18 19:36 | 46071.8167 | 2026-02-18 20:05 | 46071.8368 | 0.017671 | 0.00060935 | 22 | 638 | Planned | Planned Outage | # Shutdown for Commissioning Ring Main RMU RM218, Whangatane Drive, Kaitaia
987 |  | INCD-37076-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-02-19 02:06 | 46072.0872 | 2026-02-19 02:59 | 46072.1243 | 0.83018 | 0.020275 | 732 | 29972.65 | Unplanned | Vegetation | # Broadwood Feeder Tripped at Circuit Breaker 151922, Kaitaia Substation
988 |  | INCD-37079-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2026-03-11 12:31 | 46092.5216 | 2026-03-11 14:56 | 46092.6225 | 0.161 | 0.0011079 | 40 | 5812.6667 | Planned | Planned Outage | # Install Span to Pole 212759, SH12, Omanaia
989 |  | INCD-37088-F-MOEREWA | Moerewa 031322 - Moerewa |  | MOEREWA | 2026-02-19 13:08 | 46072.5472 | 2026-02-20 14:59 | 46073.6243 | 0.09276 | 0.00072014 | 24 | 3349 | Unplanned | Defective Equipment | # Blown Fuse near Transformer T04140, SH10, Moerewa
990 |  | INCD-37106-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2026-03-12 10:34 | 46093.4403 | 2026-03-12 15:00 | 46093.625 | 0.051573 | 0.00019388 | 7 | 1862 | Planned | Planned Outage | # Broken Crossarms, at Pole 404063, Aucks RD, Kawakawa
991 |  | INCD-37118-F-VICTORIA VALLEY | Kaitaia Transmission 151802 - Victoria Valley |  | VICTORIA VALLEY | 2026-02-21 10:35 | 46074.441 | 2026-02-21 19:02 | 46074.7931 | 0.97467 | 0.0048471 | 175 | 35189.5833 | Unplanned | Third Party | # Car vs Pole, a Pole 429008, SH1, Victoria Valley, Kaitaia
992 |  | INCD-37121-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2026-02-21 20:21 | 46074.8479 | 2026-02-21 21:53 | 46074.9118 | 0.020386 | 0.00022158 | 8 | 736 | Unplanned | Vegetation | # Vegetation in Line, at Pole 425816, Imms Rd, Kaikohe
993 |  | INCD-37139-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-03-11 09:32 | 46092.3973 | 2026-03-11 12:45 | 46092.5312 | 0.83392 | 0.0043209 | 156 | 30108 | Planned | Planned Outage | # Replace Pole, Install Isolation Points, beyond R017, Oruru Rd, Taipa
994 |  | INCD-37145-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2026-02-23 17:32 | 46076.7308 | 2026-02-23 20:52 | 46076.8694 | 0.61975 | 0.019555 | 706 | 22375.5 | Unplanned | Third Party | # Car vs Pole, at Pole 326962, Te Pua Rd, Kaikohe
995 |  | INCD-37145-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-02-23 17:32 | 46076.7308 | 2026-02-23 20:52 | 46076.8694 | 0.00075615 | 2.7698e-05 | 1 | 27.3 | Unplanned | Third Party | # Car vs Pole, at Pole 326962, Te Pua Rd, Kaikohe
996 |  | INCD-37151-F-RUSSELL EXPRESS | Kawakawa CB0209 - Russel Express |  | RUSSELL EXPRESS | 2026-03-16 09:32 | 46097.3972 | 2026-03-16 14:37 | 46097.609 | 0.2112 | 0.00069244 | 25 | 7625 | Planned | Planned Outage | # Fault Prevention, near Link L775, Manawaora, Kawakawa
997 |  | INCD-37157-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2026-03-22 09:07 | 46103.3799 | 2026-03-22 11:53 | 46103.4951 | 0.21089 | 0.0020496 | 74 | 7614 | Planned | Planned Outage | # Replace Crossarms, Pole 436293, Spring Bank Rd, Mt Pokaka
998 |  | INCD-37163-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2026-02-24 17:07 | 46077.7132 | 2026-02-24 19:03 | 46077.7937 | 0.35342 | 0.0030468 | 110 | 12760 | Unplanned | Defective Equipment | # Repair Crossarm, Beyond Switch 065, Oromahoe Rd, Mt Pokaka
999 |  | INCD-37184-F-SOUTH ROAD | Okahu CB1105 - South Road |  | SOUTH ROAD | 2026-03-16 10:01 | 46097.417 | 2026-03-16 14:07 | 46097.5883 | 0.4372 | 0.0017727 | 64 | 15784.5333 | Planned | Planned Outage | # Planned Work on Switch 4002, Sectionaliser S1334, near Pole 407704, SH1, Kaitaia
1000 |  | INCD-37184-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2026-03-16 10:01 | 46097.417 | 2026-03-16 14:07 | 46097.5883 | 0.35085 | 0.001468 | 53 | 12667 | Planned | Planned Outage | # Planned Work on Switch 4002, Sectionaliser S1334, near Pole 407704, SH1, Kaitaia
1001 |  | INCD-37187-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2026-03-30 10:30 | 46111.4375 | 2026-03-30 17:00 | 46111.7083 | 0.23765 | 0.00060935 | 22 | 8580 | Planned | Planned Outage | # Replace Conductor, Between Poles 423254 and 423269, Ruapekapeka Rd, Kawakawa
1002 |  | INCD-37199-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-03-25 09:33 | 46106.3979 | 2026-03-25 13:55 | 46106.5799 | 0.7649 | 0.0031021 | 112 | 27616 | Planned | Planned Outage | # Replace Pole 418584, Crossarms, Oruru Rd, Taipa
1003 |  | INCD-37202-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2026-02-27 14:21 | 46080.5979 | 2026-02-27 15:48 | 46080.6585 | 0.11373 | 0.0013018 | 47 | 4106.2333 | Unplanned | Wildlife | # Bird vs Line, at Sectionaliser S1057, Waihotu Rd, Omanaia
1004 |  | INCD-37205-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2026-02-27 14:25 | 46080.6009 | 2026-02-27 15:56 | 46080.6642 | 0.21192 | 0.0023266 | 84 | 7651 | Unplanned | Vegetation | # Tree vs Line, Beyond Sectionaliser S1030, Mataraua Rd, Kaikohe
1005 |  | INCD-37214-F-KAIKOHE | Kaikohe CB0107 - Kaikohe |  | KAIKOHE | 2026-02-28 03:33 | 46081.148 | 2026-02-28 04:37 | 46081.1925 | 2.2216 | 0.034622 | 1250 | 80208.3333 | Unplanned | Wildlife | # Possum Damage, at Switch 0107, Reservoir Rd, Kaikohe
1006 |  | INCD-37223-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2026-02-28 22:52 | 46081.9527 | 2026-03-01 11:59 | 46082.4993 | 1.8544 | 0.031465 | 438 | 66951.8 | Unplanned | Defective Equipment | # Broken Insulator, at Pole 433497, Rakauwahia Rd, Omanaia
1007 |  | INCD-37232-F-KARETU | Kawakawa CB0210 - Karetu |  | KARETU | 2026-03-01 11:20 | 46082.4722 | 2026-03-01 19:03 | 46082.7937 | 0.17516 | 0.0013849 | 50 | 6324 | Unplanned | Third Party | # Car vs Pole, at Pole 403887, Waikare Rd, Kawakawa
1008 |  | INCD-37238-F-ONEWHERO | Haruru CB0608 - Onewhero |  | ONEWHERO | 2026-03-01 20:53 | 46082.8698 | 2026-03-01 21:01 | 46082.8754 | 0.025728 | 0.003216 | 116.1087 | 928.87 | Unplanned | Other Cause | # Circuit Breaker CB3322 Tripped, 33kV, Haruru
1009 |  | INCD-37238-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2026-03-01 20:53 | 46082.8698 | 2026-03-01 21:01 | 46082.8754 | 0.055226 | 0.0069032 | 249.2334 | 1993.8675 | Unplanned | Other Cause | # Circuit Breaker CB3322 Tripped, 33kV, Haruru
1010 |  | INCD-37238-F-JOYCES ROAD | Haruru CB0609 - Joyces Rd |  | JOYCES ROAD | 2026-03-01 20:53 | 46082.8698 | 2026-03-01 21:01 | 46082.8754 | 0.31339 | 0.039174 | 1414.3247 | 11314.5975 | Unplanned | Other Cause | # Circuit Breaker CB3322 Tripped, 33kV, Haruru
1011 |  | INCD-37238-F-PUKETONA | Haruru CB0607 - Puketona |  | PUKETONA | 2026-03-01 20:53 | 46082.8698 | 2026-03-01 21:01 | 46082.8754 | 0.056778 | 0.0070973 | 256.24 | 2049.92 | Unplanned | Other Cause | # Circuit Breaker CB3322 Tripped, 33kV, Haruru
1012 |  | INCD-37238-F-TI BAY | Haruru CB0606 - Ti Bay |  | TI BAY | 2026-03-01 20:53 | 46082.8698 | 2026-03-01 21:01 | 46082.8754 | 0.16945 | 0.021181 | 764.7162 | 6117.73 | Unplanned | Other Cause | # Circuit Breaker CB3322 Tripped, 33kV, Haruru
1013 |  | INCD-37238-F-TE KEMARA AVE | Haruru CB0605 - Te Kemara Ave |  | TE KEMARA AVE | 2026-03-01 20:53 | 46082.8698 | 2026-03-01 21:01 | 46082.8754 | 0.08916 | 0.011145 | 402.3769 | 3219.015 | Unplanned | Other Cause | # Circuit Breaker CB3322 Tripped, 33kV, Haruru
1014 |  | INCD-37241-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2026-03-02 06:14 | 46083.2597 | 2026-03-02 09:22 | 46083.3903 | 0.031243 | 0.00016619 | 6 | 1128 | Unplanned | Wildlife | # Bird Strike, Pole 434590, Opara Rd, Omanaia
1015 |  | INCD-37244-F-BULLS GORGE | Mt Pokaka 171112 - Bulls Gorge |  | BULLS GORGE | 2026-03-02 10:38 | 46083.4431 | 2026-03-02 11:50 | 46083.4931 | 0.015954 | 0.00022158 | 8 | 576 | Unplanned | Defective Equipment | # Isolated Beyond L170 while repairing 33kV Insulator at Pole 403531, McIntyre Rd, Mt Pokaka
1016 |  | INCD-37262-F-AWANUI | NPL CB1406 - Awanui |  | AWANUI | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.72399 | 0.027338 | 987 | 26139.05 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1017 |  | INCD-37262-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.86703 | 0.032739 | 1182 | 31303.3 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1018 |  | INCD-37262-F-OXFORD STREET | Okahu CB1108 - Oxford Street |  | OXFORD STREET | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.25967 | 0.009805 | 354 | 9375.1 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1019 |  | INCD-37262-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.42325 | 0.015982 | 577 | 15280.8833 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1020 |  | INCD-37262-F-REDAN ROAD | Okahu CB1107 - Redan Road |  | REDAN ROAD | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.51934 | 0.01961 | 708 | 18750.2 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1021 |  | INCD-37262-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 1.1898 | 0.044926 | 1622 | 42955.9667 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1022 |  | INCD-37262-F-SOUTH ROAD | Okahu CB1105 - South Road |  | SOUTH ROAD | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.046946 | 0.0017727 | 64 | 1694.9333 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1023 |  | INCD-37262-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.052814 | 0.0019942 | 72 | 1906.8 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1024 |  | INCD-37262-F-VICTORIA VALLEY | Kaitaia Transmission 151802 - Victoria Valley |  | VICTORIA VALLEY | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.1379 | 0.0052072 | 188 | 4978.8667 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1025 |  | INCD-37262-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.34696 | 0.013101 | 473 | 12526.6167 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1026 |  | INCD-37262-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 1.3284 | 0.050161 | 1811 | 47961.3167 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1027 |  | INCD-37262-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.53768 | 0.020302 | 733 | 19412.2833 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1028 |  | INCD-37262-F-KAITAIA WEST | Okahu CB1106 - Kaitaia West |  | KAITAIA WEST | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.1137 | 0.0042932 | 155 | 4104.9167 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1029 |  | INCD-37262-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.49924 | 0.016923 | 611 | 18024.5 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1030 |  | INCD-37262-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.11076 | 0.0041824 | 151 | 3998.9833 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1031 |  | INCD-37262-F-PUKEPOTO | Okahu CB1110 - Pukepoto |  | PUKEPOTO | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.78121 | 0.029498 | 1065 | 28204.75 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1032 |  | INCD-37262-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.55153 | 0.018696 | 675 | 19912.5 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1033 |  | INCD-37262-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2026-03-03 13:50 | 46084.5765 | 2026-03-03 14:20 | 46084.597 | 0.82009 | 0.030966 | 1118 | 29608.3667 | Unplanned | Human Error | # Northern Area Fault, Kaitaia 33kV Substation
1034 |  | INCD-37265-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2026-03-03 16:31 | 46084.6882 | 2026-03-03 18:23 | 46084.766 | 0.34434 | 0.0030745 | 111 | 12432 | Unplanned | Defective Equipment | # Replace Crossarm at Pole 430921, Kaimaumau Rd, Pukenui
1035 |  | INCD-37268-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-03-03 18:28 | 46084.7697 | 2026-03-03 20:16 | 46084.8441 | 0.91213 | 0.0088079 | 312 | 32931.7 | Unplanned | Defective Equipment | # Defective Crossarm, at Pole 414517, Runaruna Rd, Broadwood
1036 |  | INCD-37277-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2026-03-10 09:35 | 46091.3993 | 2026-03-10 10:48 | 46091.45 | 0.020219 | 0.00027698 | 10 | 730 | Planned | Planned Outage | # Repair Conductor Between Poles 419131 - 419132, Fisher-Riley Rd, Kaitaia
1037 |  | INCD-37292-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-03-23 09:37 | 46104.4007 | 2026-03-23 14:29 | 46104.6035 | 0.16175 | 0.00055396 | 20 | 5840 | Planned | Planned Outage | # Relocate Pole 407280, Install Equipment, Broadwood Rd, Kaitaia
1038 |  | INCD-37307-F-AWARUA | Kaikohe CB0108 - Awanui |  | AWARUA | 2026-03-05 16:02 | 46086.668 | 2026-03-05 19:16 | 46086.8028 | 0.28556 | 0.0034068 | 123 | 10309.8667 | Unplanned | Defective Equipment | # Broken Crossarm, at Pole 434350, Mangakahia Rd, Kaikohe
1039 |  | INCD-37313-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-03-24 09:30 | 46105.396 | 2026-03-24 13:57 | 46105.5814 | 0.22016 | 0.00083093 | 30 | 7948.8333 | Planned | Planned Outage | # Install 3 Phase Conductor from Switch 1871, Broadwood Road, Kaitaia
1040 |  | INCD-37316-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2026-03-06 11:17 | 46087.4701 | 2026-03-06 13:56 | 46087.5806 | 0.10611 | 0.00080324 | 29 | 3831 | Unplanned | Defective Equipment | # Defective Crossarm, Pole 411571, Signal Road, Waipapa
1041 |  | INCD-37328-F-TAHEKE | Kaikohe CB0109 - Taheke |  | TAHEKE | 2026-03-10 08:39 | 46091.3604 | 2026-03-10 14:35 | 46091.6076 | 0.049302 | 0.00013849 | 5 | 1780 | Planned | Planned Outage | # Vegetation Clearance, Pole 908464, Kaikohe
1042 |  | INCD-37334-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2026-03-10 13:31 | 46091.563 | 2026-03-10 17:35 | 46091.7326 | 0.69209 | 0.0039608 | 143 | 24987.35 | Unplanned | Vegetation | # Large Branch on Line, at Pole 437877, Te Ra Road, Waipapa
1043 |  | INCD-37340-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2026-03-10 18:01 | 46091.7505 | 2026-03-10 18:51 | 46091.7852 | 0.096845 | 0.0019388 | 70 | 3496.5 | Unplanned | Defective Equipment | # Broken Crossarm at Pole 411435, Waiare Rd, Kaikohe
1044 |  | INCD-37343-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2026-03-11 04:09 | 46092.1729 | 2026-03-11 07:07 | 46092.2965 | 0.9337 | 0.014403 | 290 | 33710.35 | Unplanned | Vegetation | # Vegetation on Line at Pole 416759, Rangihoua Rd, Waipapa
1045 |  | INCD-37349-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2026-03-11 07:13 | 46092.3009 | 2026-03-11 10:35 | 46092.441 | 0.65251 | 0.004764 | 172 | 23558.1333 | Unplanned | Defective Equipment | # Broken Crossarm, Beyond Sectionaliser S1016, Whangaroa
1046 |  | INCD-37355-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2026-03-11 07:36 | 46092.3164 | 2026-03-11 08:47 | 46092.366 | 0.4759 | 0.0068136 | 246 | 17181.9667 | Unplanned | Vegetation | # Tree on Line, Beyond Sectionaliser S1007, Kerikeri Inlet Rd
1047 |  | INCD-37364-F-OROTERE | Kaeo 191772 - Orotere |  | OROTERE | 2026-03-11 09:31 | 46092.3965 | 2026-03-11 12:06 | 46092.5042 | 0.055811 | 0.00036007 | 13 | 2015 | Unplanned | Defective Equipment | # Broken Jumper, at Pole 436987, Matauri Bay Road, Kaeo
1048 |  | INCD-37367-F-OPUA | Kawakawa CB0208 - Opua |  | OPUA | 2026-03-24 09:46 | 46105.4067 | 2026-03-24 14:41 | 46105.6118 | 0.040893 | 0.00013849 | 5 | 1476.4167 | Planned | Planned Outage | # Fault Prevention, Replace Poles 402578, 402577, Smeath Rd, Kawakawa
1049 |  | INCD-37385-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-03-12 00:31 | 46093.0212 | 2026-03-12 04:05 | 46093.1703 | 1.5 | 0.0094726 | 342 | 54156.15 | Unplanned | Vegetation | # Branch on Line, at Pole 421840, Oruru Rd, Taipa
1050 |  | INCD-37388-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2026-03-12 00:37 | 46093.0256 | 2026-03-12 10:13 | 46093.4257 | 1.1435 | 0.015982 | 577 | 41286.45 | Unplanned | Defective Equipment | # Binder off Crossarm, at Pole 429619, Church Road, Kaitaia
1051 |  | INCD-37388-F-CLOUGH ROAD | Kaitaia Transmission 151822 - Clough Road |  | CLOUGH ROAD | 2026-03-12 00:37 | 46093.0256 | 2026-03-12 10:13 | 46093.4257 | 0.60639 | 0.010442 | 377 | 21893.1167 | Unplanned | Defective Equipment | # Binder off Crossarm, at Pole 429619, Church Road, Kaitaia
1052 |  | INCD-37394-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2026-03-12 12:03 | 46093.5021 | 2026-03-12 13:24 | 46093.5583 | 0.091984 | 0.0011356 | 41 | 3321 | Unplanned | Defective Equipment | # Repair Broken Crossarm on Pole 435813, Henderson Bay Road, Pukenui
1053 |  | INCD-37403-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2026-03-13 09:46 | 46094.4069 | 2026-03-13 14:46 | 46094.6153 | 1.6438 | 0.0154 | 556 | 59346 | Unplanned | Defective Equipment | # Line Down at Pole 341031, SH12, Opononi
1054 |  | INCD-37409-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2026-03-13 11:51 | 46094.4938 | 2026-03-13 13:21 | 46094.5563 | 0.089741 | 0.00099712 | 36 | 3240 | Unplanned | Defective Equipment | # Broken Crossarm, at Transformer T04188, Whangape Rd, Kaitaia
1055 |  | INCD-37418-F-MATAURI BAY | Kaeo 191732 - Matauri Bay |  | MATAURI BAY | 2026-03-13 14:47 | 46094.616 | 2026-03-13 17:03 | 46094.7104 | 0.14641 | 0.0014126 | 51 | 5286 | Unplanned | Defective Equipment | # Broken Crossarm, at Pole 433028, Matauri Bay Road
1056 |  | INCD-37463-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2026-03-18 08:11 | 46099.341 | 2026-03-18 08:51 | 46099.3688 | 0.16743 | 0.0041824 | 151 | 6045.0333 | Unplanned | Wildlife | # Bird vs Line, at Pole 419497, Fairburn Rd, Kaitaia
1057 |  | INCD-37481-F-POKAPU | Moerewa 031312 - Pokapu |  | POKAPU | 2026-03-19 12:46 | 46100.532 | 2026-03-19 15:27 | 46100.6438 | 0.23182 | 0.0041547 | 150 | 8369.6 | Unplanned | Third Party | # Vehicle hit Lines at Pole 420643, Ngapipito Rd, Moerewa
1058 |  | INCD-37487-F-POKAPU | Moerewa 031312 - Pokapu |  | POKAPU | 2026-03-20 07:32 | 46101.3139 | 2026-03-20 08:58 | 46101.3736 | 0.078606 | 0.00091403 | 33 | 2838 | Unplanned | Wildlife | # Bird vs Poles, Pole 425282, Pokapu Rd, Moerwa
1059 |  | INCD-37511-F-CROSSROADS | Mt Pokaka 171122 - Crossroads |  | CROSSROADS | 2026-03-22 12:16 | 46103.5111 | 2026-03-22 13:07 | 46103.5465 | 0.07628 | 0.0014957 | 54 | 2754 | Unplanned | Defective Equipment | # Defective Equipment, at Fuse F_T01996, Springbank Rd, Mt Pokaka
1060 |  | INCD-37526-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-03-23 16:49 | 46104.7007 | 2026-03-23 18:18 | 46104.7625 | 0.085309 | 0.0012187 | 44 | 3080 | Unplanned | Defective Equipment | # Repair Crossarm, at Pole 414615, Motuti Rd, Kaitaia
1061 |  | INCD-37529-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2026-03-23 17:59 | 46104.7493 | 2026-03-23 22:03 | 46104.9187 | 0.0067583 | 2.7698e-05 | 1 | 244 | Unplanned | Defective Equipment | # SWER Line Beyond L588 Down, Te Tio Rd, Kaikohe
1062 |  | INCD-37544-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-03-24 10:42 | 46105.4458 | 2026-03-24 14:38 | 46105.6097 | 0.091513 | 0.00038777 | 14 | 3304 | Unplanned | Vegetation | # Repair Broken Line, at Pole 419392, Paranui Rd, Taipa
1063 |  | INCD-37553-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-03-25 06:29 | 46106.2701 | 2026-03-25 10:21 | 46106.4313 | 0.0015017 | 2.7698e-05 | 0.92418 | 54.2167 | Unplanned | Defective Equipment | # Broken Crossarm, Pole 411220, SH1, Kaikohe
1064 |  | INCD-37553-F-RANGIAHUA | Kaikohe CB0105 - Rangiahua |  | RANGIAHUA | 2026-03-25 06:29 | 46106.2701 | 2026-03-25 10:21 | 46106.4313 | 1.2661 | 0.021161 | 706.0758 | 45712 | Unplanned | Defective Equipment | # Broken Crossarm, Pole 411220, SH1, Kaikohe
1065 |  | INCD-37556-F-KAIKOHE | Kaikohe CB0107 - Kaikohe |  | KAIKOHE | 2026-03-25 08:36 | 46106.3581 | 2026-03-25 10:42 | 46106.4458 | 3.4847 | 0.034705 | 1253 | 125811.4833 | Unplanned | Unknown | # Circuit Breaker CB0107 Tripped, Reservoir Rd, Kaikohe
1066 |  | INCD-37565-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2026-03-25 12:48 | 46106.5333 | 2026-03-25 18:54 | 46106.7875 | 0.030412 | 8.3093e-05 | 3 | 1098 | Unplanned | Adverse Weather | # Line Down, at Pole 409155, Waiare Rd, Waipapa
1067 |  | INCD-37571-F-PUKENUI SOUTH | Pukenui 131132 - Pukenui South |  | PUKENUI SOUTH | 2026-03-25 14:46 | 46106.6156 | 2026-03-25 18:00 | 46106.75 | 0.74302 | 0.023571 | 612 | 26825.8333 | Unplanned | Vegetation | # Tree through Line, Pole 432693, Hukatere Rd, Pukenui
1068 |  | INCD-37574-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2026-03-25 15:46 | 46106.6569 | 2026-03-25 18:58 | 46106.7903 | 0.26029 | 0.002659 | 96 | 9397.5167 | Unplanned | Defective Equipment | # Crossarm Failed at Pole 418381, Inland Rd, Taipa
1069 |  | INCD-37577-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2026-03-25 16:15 | 46106.6771 | 2026-03-26 11:27 | 46107.4771 | 0.42504 | 0.0014957 | 54 | 15345.7333 | Unplanned | Adverse Weather | # Suspension Clamp Failure, Pole 405615, SH12, Omanaia
1070 |  | INCD-37580-F-TE KAO | Pukenui 131142 - Te Kao |  | TE KAO | 2026-03-25 17:13 | 46106.7174 | 2026-03-25 21:12 | 46106.8833 | 2.0603 | 0.0097219 | 351 | 74385 | Unplanned | Defective Equipment | # Broken Crossarm, Pole 435504 Far North Rd, Pukenui
1071 |  | INCD-37589-F-RAWENE | Omanaia 051742 - Rawene |  | RAWENE | 2026-03-25 22:01 | 46106.9174 | 2026-03-28 15:15 | 46109.6354 | 0.018117 | 0.0013018 | 30.3214 | 654.0833 | Unplanned | Adverse Environment | # Multiple Faults, Wekaweka Rd, Waimamaku
1072 |  | INCD-37589-F-OPONONI | Omanaia 051762 - Opononi |  | OPONONI | 2026-03-25 22:01 | 46106.9174 | 2026-03-28 15:15 | 46109.6354 | 10.1795 | 0.03044 | 709.004 | 367522.4 | Unplanned | Adverse Environment | # Multiple Faults, Wekaweka Rd, Waimamaku
1073 |  | INCD-37589-F-BROADWOOD | Kaitaia Transmission 151922 - Broadwood |  | BROADWOOD | 2026-03-25 22:01 | 46106.9174 | 2026-03-28 15:15 | 46109.6354 | 3.0124 | 0.0029914 | 69.6746 | 108760 | Unplanned | Adverse Environment | # Multiple Faults, Wekaweka Rd, Waimamaku
1074 |  | INCD-37598-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-03-26 01:28 | 46107.0609 | 2026-03-26 05:48 | 46107.2417 | 5.5301 | 0.032683 | 1180 | 199658.5333 | Unplanned | Vegetation | # Vegetation Tripped Kaitaia to Taipa 33kV Line, SH1, Taipa
1075 |  | INCD-37598-F-TAIPALS | Taipa CB1205 - Tokerau |  | TAIPALS | 2026-03-26 01:28 | 46107.0609 | 2026-03-26 05:48 | 46107.2417 | 8.093 | 0.044981 | 1624 | 292190.25 | Unplanned | Vegetation | # Vegetation Tripped Kaitaia to Taipa 33kV Line, SH1, Taipa
1076 |  | INCD-37598-F-MANGONUI | Taipa CB1208 - Mangonui |  | MANGONUI | 2026-03-26 01:28 | 46107.0609 | 2026-03-26 05:48 | 46107.2417 | 5.9133 | 0.050133 | 1810 | 213492.3333 | Unplanned | Vegetation | # Vegetation Tripped Kaitaia to Taipa 33kV Line, SH1, Taipa
1077 |  | INCD-37604-F-TAKOU BAY | Waipapa 041672 - Takou Bay |  | TAKOU BAY | 2026-03-26 08:12 | 46107.3416 | 2026-03-26 11:30 | 46107.4791 | 0.95768 | 0.020746 | 608 | 34576 | Unplanned | Unknown | # Fuse F2009 Tripped due to Private Property Equipment, Takou Bay Rd, Waipapa
1078 |  | INCD-37613-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-03-26 09:15 | 46107.3856 | 2026-03-27 09:13 | 46108.384 | 0.68859 | 0.014569 | 326.3455 | 24860.8167 | Unplanned | Vegetation | # Tree on Line, Pole 418890, Kopuokai Rd, Kaitaia
1079 |  | INCD-37613-F-FAIRBURN ROAD | Kaitaia Transmission 151902 - Fairburn Road |  | FAIRBURN ROAD | 2026-03-26 09:15 | 46107.3856 | 2026-03-27 09:13 | 46108.384 | 1.6231 | 0.0073953 | 165.6545 | 58599.2 | Unplanned | Vegetation | # Tree on Line, Pole 418890, Kopuokai Rd, Kaitaia
1080 |  | INCD-37616-F-TOTARA NORTH | Kaeo 191782 - Totara North |  | TOTARA NORTH | 2026-03-19 11:53 | 46100.4951 | 2026-03-26 11:44 | 46107.4889 | 0.19893 | 0.0023266 | 84 | 7182 | Unplanned | Vegetation | # Line Down, at Pole 410263, Otangaroa Rd, Kaeo
1081 |  | INCD-37619-F-PUKETI | Waipapa 041692 - Puketi |  | PUKETI | 2026-03-26 10:20 | 46107.4306 | 2026-03-26 11:51 | 46107.4938 | 0.012242 | 0.00013849 | 5 | 442 | Unplanned | Unknown | # Blown Fuse F2086, Waipapa Loop Rd, Waipapa
1082 |  | INCD-37622-F-INLET ROAD | Kerikeri 181142 - Inlet Road |  | INLET ROAD | 2026-03-26 10:22 | 46107.4318 | 2026-03-26 13:42 | 46107.5708 | 0.89299 | 0.0095834 | 346 | 32240.5333 | Unplanned | Defective Equipment | # Line Down at Pole 401824, Kerikeri Inlet Rd, Kerikeri
1083 |  | INCD-37664-F-SHEPHERD ROAD | Kerikeri 181192 - Shepherd Road |  | SHEPHERD ROAD | 2026-03-26 16:54 | 46107.7039 | 2026-03-26 17:04 | 46107.7109 | 0.073953 | 0.0073953 | 267 | 2670 | Unplanned | Vegetation | # Branch on Line, at Pole 401231, Shepherd Rd, Kerikeri
1084 |  | INCD-37673-F-TOWAI | Kawakawa CB0206 - Towai |  | TOWAI | 2026-03-26 21:26 | 46107.8933 | 2026-03-27 14:19 | 46108.5965 | 2.6083 | 0.0025759 | 93 | 94171.8 | Unplanned | Defective Equipment | # Broken Pole during Storm, Callaghan Rd, Kawakawa
1085 |  | INCD-37676-F-PURERUA | Waipapa 041632 - Purerua |  | PURERUA | 2026-03-26 23:13 | 46107.9671 | 2026-03-27 07:39 | 46108.3187 | 2.6932 | 0.005318 | 192 | 97235.2 | Unplanned | Adverse Weather | # Adverse Weather Tripped Sectionaliser S1044, Opito Bay Rd, Waipapa
1086 |  | INCD-37682-F-ORURU | Taipa CB1206 - Oruru |  | ORURU | 2026-03-26 23:43 | 46107.9882 | 2026-03-27 08:21 | 46108.3479 | 0.24391 | 0.00047086 | 17 | 8806 | Unplanned | Adverse Weather | # Adverse Weather, Tripped Fuse F2520, Sawyers Rd, Taipa
1087 |  | INCD-37691-F-NORTH ROAD | NPL CB1408 - North Road |  | NORTH ROAD | 2026-03-26 22:44 | 46107.9472 | 2026-03-28 16:09 | 46109.6729 | 1.0166 | 0.0047917 | 80 | 36703.0667 | Unplanned | Adverse Environment | # Blown Fuses at RM115, due to Submerged Transformers, T05401, North Park Drive, Kaitaia
1088 |  | INCD-37694-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2026-03-27 10:41 | 46108.4451 | 2026-03-27 13:35 | 46108.566 | 0.24438 | 0.001468 | 53 | 8823 | Unplanned | Adverse Environment | # Emergency Isolation, Pole 407818 Gave Way due to Slip, SH1, Kaitaia
1089 |  | INCD-37703-F-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2026-03-27 15:20 | 46108.6389 | 2026-03-27 18:23 | 46108.766 | 0.030412 | 0.00016619 | 6 | 1098 | Unplanned | Vegetation | # Tree on Line, Pole 419854, Okaka Rd, Waimate North
1090 |  | INCD-37715-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2026-03-28 14:39 | 46109.6104 | 2026-03-28 17:45 | 46109.7396 | 0.15971 | 0.00085863 | 31 | 5766 | Unplanned | Adverse Weather | # Recloser R_T05695 Tripped, Waipa Valley Rd, Omanaia
1091 |  | INCD-37718-F-RANGITIHI | Kaitaia Transmission 151912 - Rangitihi |  | RANGITIHI | 2026-03-30 11:56 | 46111.4972 | 2026-03-30 15:19 | 46111.6382 | 0.29711 | 0.001468 | 53 | 10727 | Planned | Planned Outage | # Replace Pole 407818, SH1, Kaitaia
1092 |  | INCD-37730-F-VICTORIA VALLEY | Kaitaia Transmission 151802 - Victoria Valley |  | VICTORIA VALLEY | 2026-03-29 10:14 | 46110.4264 | 2026-03-29 11:16 | 46110.4692 | 0.29899 | 0.0048471 | 175 | 10794.5833 | Unplanned | Defective Equipment | # Crossarm failed at Transformer T02402, SH1, Kaitaia
1093 |  | INCD-37754-F-HEREKINO | Okahu CB1109 - Herekino |  | HEREKINO | 2026-03-30 02:05 | 46111.0869 | 2026-03-30 15:40 | 46111.6528 | 4.7666 | 0.0066198 | 239 | 172095 | Unplanned | Adverse Environment | # Transformer, Pole Fell into River, at T00367, Kaitaia Awaroa Rd, Kaitaia
1094 |  | INCD-37760-F-WAIMA | Omanaia 051772 - Waima |  | WAIMA | 2026-03-30 09:24 | 46111.3916 | 2026-03-30 16:14 | 46111.6764 | 1.2599 | 0.016175 | 438 | 45487.8667 | Unplanned | Third Party | # Car vs Pole, at Pole 433629, SH12, Taheke
1095 |  | INCD-551-K-HOREKE | Kaikohe CB0111 - Horeke |  | HOREKE | 2026-03-15 18:39 | 46096.7771 | 2026-03-15 21:14 | 46096.8847 | 0.025759 | 0.00016619 | 6 | 930 | Unplanned | Vegetation | # Vegetation on Line, at Pole 419844, Okaka Rd, Kaikohe
1096
1097 |  | Total | 1088 | [6 empty] | 1510.771 | 8.9401 |  | 54544875.2502
1098 |  | ¹ Extend table as necessary to disclose information for all individual interruptions
Formulas:
Start date (dd/mm/yyyy) = IFERROR(INDEX([1]!v_s10a_incident_by_feeder_FY26[Start_Date], ROWS(I9:[Start date (dd/mm/yyyy)])),"")
End date (dd/mm/yyyy) = IFERROR(INDEX([1]!v_s10a_incident_by_feeder_FY26[End_Date], ROWS(K9:[End date (dd/mm/yyyy)])),"")